## InfraPower
OID | Name | Access Type | Description
.1.3.6.1.4.1.34550.20 | InfraPower | N/A | N/A
.1.3.6.1.4.1.34550.20.1 | ipDongle | N/A | N/A
.1.3.6.1.4.1.34550.20.1.1 | ipDongleAdmin | N/A | N/A
.1.3.6.1.4.1.34550.20.1.1.1.0 | ipdongleModel | Read Only | InfraPower
.1.3.6.1.4.1.34550.20.1.1.5.0 | ipdongleName | Read / Write | The name of the IP Dongle Length : 4 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.1.1.6.0 | ipdongleLocation | Read / Write | The Location of the IP Dongle Length : 4 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.1.1.8.0 | ipdongleMacAddress | Read Only | The MAC address of the IP Dongle
.1.3.6.1.4.1.34550.20.1.1.9.0 | ipdongleIpAddressIpv4 | Read Only | The IPv4 address of the IP Dongle
.1.3.6.1.4.1.34550.20.1.1.10.0 | ipdongleSubnetIpv4 | Read Only | The IPv4 subnet of the IP Dongle
.1.3.6.1.4.1.34550.20.1.1.11.0 | ipdongleGatewayIpv4 | Read Only | The IPv4 gateway of the IP Dongle
.1.3.6.1.4.1.34550.20.2 | pduGroup | N/A | N/A
.1.3.6.1.4.1.34550.20.2.1 | pduAdmin | N/A | N/A
.1.3.6.1.4.1.34550.20.2.1.1 | pduTable | N/A | Table of PDU
.1.3.6.1.4.1.34550.20.2.1.1.1 | pduEntry | N/A | Table Entries of PDU
.1.3.6.1.4.1.34550.20.2.1.1.1.1.[1..32] | pduIndex | Read Only | PDU level in the Group , Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.1.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.1.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.1.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.1.17 = Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.2.[1..32] | pduModel | Read Only | PDU model No. , Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.2.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.2.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.2.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.2.17 = Feed 2 of PDU level 1 ( Feed 1 and Feed 2 of Dual Feed PDU will show the same PDU model )
.1.3.6.1.4.1.34550.20.2.1.1.1.3.[1..32] | pduID | Read Only | PDU unique identifier , Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.3.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.3.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.3.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.3.17 = Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.4.[1..32] | pduSerialNo | Read Only | PDU Serial no. ( This OID is NOT applicable to PDU with 1.8" color LCD & the value of the OID returned will be BLANK ), Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.4.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.4.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.4.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.4.17 = Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.6.[1..32] | pduName | Read / Write | The name of PDU , Level : 1 to 16 Length : 1 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) , ( . ) and ( space ) Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.6.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.6.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.6.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.6.17 = Feed 2 of PDU level 1 ( Feed 1 and Feed 2 of Dual Feed PDU will show the same PDU name )
.1.3.6.1.4.1.34550.20.2.1.1.1.7.[1..32] | pduLocation | Read / Write | The Location of PDU , Level : 1 to 16 Length : 1 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) , ( . ) and ( space ) Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.7.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.7.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.7.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.7.17 = Feed 2 of PDU level 1 ( Feed 1 and Feed 2 of Dual Feed PDU will show the same PDU Location )
.1.3.6.1.4.1.34550.20.2.1.1.1.8.[1..32] | pduGroupNumber | Read / Write | The number indicates the IP dongle group the PDU belongs to when using InfraPower Management Software. Group number : from 000 to 240
.1.3.6.1.4.1.34550.20.2.1.1.1.13.[1..32] | pduMainLoadVoltage | Read Only | The voltage measured of the PDU in tenth of Volts , Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.13.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.13.16 = PDU level 16 Single Phase PDU : 2215 = 221.5 VAC 3 Phase PDU : 2204 ( 2201 , 2205 , 2206 ) = 1st 4 digit is the average voltage of all the phase. The figure in the bracket is the voltage of phase 1 , phase 2 & phase 3 respectively Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.1.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.1.17 = Feed 2 of PDU level 17 Single Phase PDU : 2215 = 221.5 VAC
.1.3.6.1.4.1.34550.20.2.1.1.1.14.[1..32] | pduMainLoadAmp | Read Only | The current load ampere of the PDU measured in tenth of amp. 0 = 0.0A , 1 = 0.1A , 135 = 13.5A Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.14.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.14.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.14.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.14.17 = Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.16.[1..32] | pduMainPowerFactor | Read Only | The power factor of the PDU measured in hundredth 000 = 0 , 001 = 0.01 , 055 = 0.55 , 100 = 1.0 Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.16.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.16.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.16.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.16.17 = Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.17.[1..32] | pduMainActivePower | Read Only | The power consumption of the PDU measured in hundred-thousandth of kW Range : 0000000 to 9999999 0 = 0kW , 25 = 0.00025kW , 123 = 0.00123kW , 1234567 = 12.34567kW Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.17.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.17.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.17.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.17.17 = Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.18.[1..32] | pduMainApparentPower | Read Only | The power consumption of the PDU measured in hundred-thousandth of kVA Range : 0000000 to 9999999 0 = 0VA , 25 = 0.25VA, 123 = 1.23VA , 1234567 = 12345.67VA Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.18.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.18.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.18.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.18.17 = Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.19.[1..32] | pduMainCumulativeEnergy | Read Only | The accumulated energy consumption of the PDU in hundredth of kWh Range : 00000000 to 99999999 0 = 0.00kWh , 123 = 1.23kWh , 12345 = 123.45kWh , 12345678 = 123456.78kWh Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.19.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.19.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.19.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.19.17 = Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.20.[1..32] | pduRealClock | Read Only | The real time of the PDU. Format : YYMMDDHHNNSSW 1503281759596 = 2015-Mar-28 17:59:59 Saturaday
.1.3.6.1.4.1.34550.20.2.1.1.1.24 | circuits | N/A
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1 | circuitTable | N/A | Table of circuits / banks
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1 | circuitTablEntry | N/A | Table entries of circuit / bank
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.1.[1..32].[1..6] | circuitIndex | Read Only | The ID of the PDU's circuit / bank Single Feed PDU : Single Phase : 1 = Circuit A , 2= Circuit B 63A Single Phase : 1 = bank 1 , 2 = bank 2 , 3 = bank 3 , 4 = bank 4 3 Phase : 1 = bank 1 , 2 = bank 2 , 3 = bank 3 , 4 = bank 4, 5 = bank 5 , 6 = bank 6 Dual Feed PDU : Single Phase : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.1.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.1.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.2.[1..32].[1..6] | circuitRatedAmp | Read Only | The input current rating of the PDU's circuit / bank in tenth of amp. Single Feed PDU : 100 = 10.0A , 160 = 16.0A , 200 = 20.0A Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.2.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.2.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.4.[1..32].[1..6] | circuitName | Read Only | The name of the circuit Single Feed PDU : Single Phase : Circuit A , Circuit B 63A Single Phase : Circuit B1 , Circuit B2 , Circuit B3 , Circuit B4 3 Phase ( 400V ) : L1-B1, L1-B2 , L2-B3, L2-B4, L3-B5, L3-B6 3 Phase ( 208V ) : B1 , B2 , B3 , B4 , B5 , B6 Dual Feed PDU : Single Phase : PDU I - A , PDU I - B , PDU II - A , PDU II - B
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.5.[1..32].[1..6] | circuitState | Read Only | The status of the PDU's circuit / bank. Single Feed PDU : 0 = Normal, 1 = Alarm , 2 = Rising alert , 3 = Low alert , 4 = circuit not exist Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.5.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.5.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.6.[1..32].[1..6] | circuitLoadVoltage | Read Only | The voltage of the PDU's circuit / bank measured in tenth of volt. 0000 = 0.0VAC , 1100 = 110.0VAC , 2225 = 222.5VAC Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.6.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.6.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.7.[1..32].[1..6] | circuitLoadAmp | Read Only | The current load ampere of the PDU's circuit / bank measured in tenth of amp. 000 = 0.0A , 001 = 0.01A , 105 = 10.5A Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.7.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.7.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.9.[1..32].[1..6] | circuitPowerFactor | Read Only | The power factor of the PDU's circuit measured in hundredth 000 = 0 , 001 = 0.01 , 055 = 0.55 , 100 = 1.0 Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.9.1.1 = circuit A of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.9.16.2 = circuit B of PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.9.1.1 = circuit A of Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.9.17.2 = circuit B of Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.10.[1..32].[1..6] | circuitActivePower | Read Only | The power consumption of the PDU's circuit measured in hundred-thousandth of kW Range : 0000000 to 9999999 0 = 0kW , 25 = 0.00025kW , 123 = 0.00123kW , 1234567 = 12.34567kW Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.10.1.1 = circuit A of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.10.16.2 = circuit B of PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.10.1.1 = circuit A of Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.10.17.2 = circuit B of Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.11.[1..32].[1..6] | circuitApparentPower | Read Only | The power consumption of the PDU's circuit measured in hundred-thousandth of kVA Range : 0000000 to 9999999 0 = 0VA , 25 = 0.25VA, 123 = 1.23VA , 1234567 = 12345.67VA Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.11.1.1 = circuit A of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.11.16.2 = circuit B of PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.11.1.1 = circuit A of Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.11.17.2 = circuit B of Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.12.[1..32].[1..6] | circuitLoadPeakAmp | Read Only | The peak load ampere of the PDU's circuit / bank recorded in tenth of amp with timestamp. 150330105959@081 = 2015-Mar-30 10:59:59 , 8.1A Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.12.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.12.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.13.[1..32].[1..6] | circuitCumulativeEnergy | Read Only | The accumulated energy consumption of the PDU's circuit / bank in hundredth of kWh with timestamp Range : 00000000 to 99999999 150330105959@09999999 = 2015-Mar-30 10:59:59 , 99999.99kWh Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.13.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.13.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.14.[1..32].[1..6] | circuitLoadPeakAmpReset | Read / Write | To reset the PDU's circuit / bank peak amp to zero with timestamp updated. Set : 1 = confirm to reset Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.14.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.14.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.15.[1..32].[1..6] | circuitBreakerStateCopy | Read Only | The circuit breaker state of the PDU. 0 = normal , 1 = tripped Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.15.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.15.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.16.[1..32].[1..6] | circuitLoadAmpAlarmThresh | Read / Write | To set the current load ampere alarm threshold of the PDU's circuit / bank in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.16.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.16.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.17.[1..32].[1..6] | circuitLoadAmpRisingAlertThresh | Read / Write | To set the current load ampere rising alert threshold of the PDU's circuit / bank in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.17.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.17.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.18.[1..32].[1..6] | circuitLoadAmpLowAlertThresh | Read / Write | To set the current load ampere low alert threshold of the PDU's circuit / bank in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.18.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.18.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.19.[1..32].[1..6] | circuitCumulativeEnergyReset | Read / Write | To reset the PDU's circuit / bank cumulative energy to zero with timestamp updated. Set : 1 = confirm to reset Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.19.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.19.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.25 | circuitBreakers | N/A
.1.3.6.1.4.1.34550.20.2.1.1.1.25.1 | circuitBreakerTable | N/A | Table of circuit breaker
.1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1 | circuitBreakerTableEntry | N/A | Table entries of circuit breaker
.1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.1.[1..32].[1..6] | circuitBreakerIndex | Read Only | The ID of the PDU's circuit breaker. Single Phase : 1 = circuit A's circuit breaker, 2 = circuit B's circuit breaker 63A Single Phase : 1 = bank 1's circuit breaker , 2 = bank 2's circuit breaker , 3 = bank 3's circuit breaker , 4 = bank 4's circuit breaker 3 Phase : 1 = bank 1's circuit breaker , 2 = bank 2's circuit breaker , 3 = bank 3's circuit breaker , 4 = bank 4's circuit breaker , 5 = bank 5's circuit breaker , 6 = bank 6's circuit breaker Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.1.16.1 = circuit A's circuit breaker of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.1.32.1 = circuit A's circuit breaker of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.2.[1..32].[1..6] | circuitBreakerRatedAmp | Read Only | The current rating of the PDU's circuit breaker in tenth of amp. 100 = 10.0A , 160 = 16.0A , 200 = 20.0A Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.2.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.2.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.4.[1..32].[1..6] | circuitBreakerState | Read Only | The circuit breaker state of the PDU. 0 = normal , 1 = tripped Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.4.16.1 = circuit A's circuit breaker of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.4.32.1 = circuit A's circuit breaker of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.26 | outlets | N/A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1 | stdOutletTable | N/A | Table of non - C19 outlet
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1 | stdOutletTableEntry | N/A | Table entries of non - C19 outlet
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.1.[1..32].[1..72] | stdOutletIndex | Read Only | The ID of the PDU's non - C19 outlet. Range : 1 to 72. 1 = outlet 01, 72 = outlet 72
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.2.[1..32].[1..72] | stdOutletCircuit | Read Only | The circuit of the outlet belongs to - Single phase : 1 = circuit A , 2 = circuit B 63A single phase : 1 = bank 1 , 2 = bank 2 , 3 = bank , 4 = bank 4 3 Phase : 1 = bank 1 , 2 = bank 2 , 3 = bank , 4 = bank 4 , 5 = bank 5 , 6 = bank 6 Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.2.16.1 = outlet 1 of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.2.32.16 = outlet 16 ofFeed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.3.[1..32].[1..72] | stdOutletType | Read Only | The type of non - C19 outlet. 1 = IEC C13 , 3 = BS1363 , 4 = NEMA 5-204 , 5 = Schuko , 6 = AS 31125 , 7 = French , 8 = 60309-16A , 9 =60309-32A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.4.[1..32].[1..72] | stdOutletName | Read / Write | The name of the outlet. Range : 4 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) , ( . ) and ( space )
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.7.[1..32].[1..72] | stdOutletPowerStatus | Read / Write | The power state of the outlet. 0 = OFF , 1 = ON Set : 0 = switch off , 1 = switch on
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.8.[1..32].[1..72] | stdOutletAlarmState | Read Only | The alarm state of the outlet. 0 = Normal, 1 = Alarm , 2 = Rising alert , 3 = Low alert
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.9.[1..32].[1..72] | stdOutletLoadAmp | Read Only | The current load ampere of the outlet measured in tenth of amp. 000 = 0.0A , 001 = 0.01A , 105 = 10.5A , " --- " = immeasurable
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.10.[1..32].[1..72] | stdOutletEnergy | Read Only | The power consumption of the OUTLET measured in hundred-thousandth of kW. Range : 0000000 to 9999999 0 = 0kW , 25 = 0.00025kW , 123 = 0.00123kW , 1234567 = 12.34567kW
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.11.[1..32].[1..72] | stdOutletPeakAmp | Read Only | The peak load ampere of the outlet recorded in tenth of amp with timestamp. 150330105959@031 = 2015-Mar-30 10:59:59 , 3.1A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.12.[1..32].[1..72] | stdOutletCumulativeEnergy | Read Only | The accumulated energy consumption of the outlet in hundredth of kWh with timestamp Range : 00000000 to 99999999 150330105959@09999999 = 2015-Mar-30 10:59:59 , 99999.99kWh
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.13.[1..32].[1..72] | stdOutletLoadAmpAlarmThresh | Read / Write | To set the current load ampere alarm threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.14.[1..32].[1..72] | stdOutletLoadAmpRisingAlertThresh | Read / Write | To set the current load ampere rising alert threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.15.[1..32].[1..72] | stdOutletLoadAmpLowAlertThresh | Read / Write | To set the current load ampere low alert threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.16.[1..32].[1..72] | stdOutletPeakAmpReset | Read / Write | To reset the outlet peak amp reacord to zero with timestamp updated. Set : 1 = confirm to reset
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.17.[1..32].[1..72] | stdOutletCumulativeEnergyReset | Read / Write | To reset the outlet accumulated energy consumpiton record to zero with timestamp updated. Set : 1 = confirm to reset
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.18.[1..32].[1..72] | stdOutletPowerUpSequenceDelay | Read / Write | To set the sequential power up interval between outlet in second. Range : 1 to 10 sec. Set : 0 = 1 sec , 5 = 6 sec , 9 = 10 sec
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2 | c19OutletTable | N/A | Table of C19 outlet
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1 | c19OutletTableEntry | N/A | Table entries of C19 outlet
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.1.[1..32].[1..72] | c19OutletIndex | Read Only | The ID of the PDU's C19 outlet. Range : 1 to 72. 1 = outlet C01, 72 = outlet C72
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.2.[1..32.[1..72] | c19OutletCircuit | Read Only | The circuit of the outlet belongs to - Single phase : 1 = circuit A , 2 = circuit B 63A single phase : 1 = bank 1 , 2 = bank 2 , 3 = bank , 4 = bank 4 3 Phase : 1 = bank 1 , 2 = bank 2 , 3 = bank , 4 = bank 4 , 5 = bank 5 , 6 = bank 6 Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.2.16.1 = outlet C1 of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.2.32.16 = outlet C16 of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.3.[1..32].[1..72] | c19OutletType | Read Only | The type of C19 outlet. 2 = IEC C19
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.4.[1..32].[1..72] | c19OutletName | Read / Write | The name of the outlet. Range 4 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) , ( . ) and ( space )
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.7.[1..32].[1..72] | c19OutletPowerStatus | Read / Write | The power state of the outlet. 0 = OFF , 1 = ON Set : 0 = switch off , 1 = switch on
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.8.[1..32].[1..72] | c19OutletAlarmState | Read Only | The alarm state of the outlet. 0 = Normal, 1 = Alarm , 2 = Rising alert , 3 = Low alert
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.9.[1..32].[1..72] | c19OutletLoadAmp | Read Only | The current load ampere of the outlet measured in tenth of amp. 000 = 0.0A , 001 = 0.01A , 105 = 10.5A , " --- " = immeasurable
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.10.[1..32].[1..72] | c19OutletEnergy | Read Only | The power consumption of the OUTLET measured in hundred-thousandth of kW. Range : 0000000 to 9999999 0 = 0kW , 25 = 0.00025kW , 123 = 0.00123kW , 1234567 = 12.34567kW
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.11.[1..32].[1..72] | c19OutletPeakAmp | Read Only | The peak load ampere of the outlet recorded in tenth of amp with timestamp. 150330105959@031 = 2015-Mar-30 10:59:59 , 3.1A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.12.[1..32].[1..72] | c19OutletCumulativeEnergy | Read Only | The accumulated energy consumption of the outlet in hundredth of kWh with timestamp Range : 00000000 to 99999999 150330105959@09999999 = 2015-Mar-30 10:59:59 , 99999.99kWh
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.13.[1..32].[1..72] | c19OutletLoadAmpAlarmThresh | Read / Write | To set the current load ampere alarm threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.14.[1..32].[1..72] | c19OutletLoadAmpRisingAlertThresh | Read / Write | To set the current load ampere rising alert threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.15.[1..32].[1..72] | c19OutletLoadAmpLowAlertThresh | Read / Write | To set the current load ampere low alert threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.16.[1..32].[1..72] | c19OutletPeakAmpReset | Read / Write | To reset the outlet peak amp reacord to zero with timestamp updated. Set : 1 = confirm to reset
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.17.[1..32].[1..72] | c19OutletCumulativeEnergyReset | Read / Write | To reset the outlet accumulated energy consumpiton record to zero with timestamp updated. Set : 1 = confirm to reset
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.18.[1..32].[1..72] | c19OutletPowerUpSequenceDelay | Read / Write | To set the sequential power up interval between outlet in second. Range : 1 to 10 sec. Set : 0 = 1 sec , 5 = 6 sec , 9 = 10 sec
.1.3.6.1.4.1.34550.20.2.1.1.1.27 | THSensors | N/A
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1 | THSensorsTable | N/A | Table of TH sensors
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1 | THSensorsTableEntry | N/A | Table entries of TH sensors
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.1.[1..16].[1..2] | THSensorIndex | Read Only | The ID of TH sensors. 1 = TH 1 , 2 = TH 2
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.3.[1..16].[1..2] | THSensorLocation | Read / Write | The location of TH sensor. Range : 4 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.4.[1..16].[1..2] | THSensorType | Read Only | The type of the sensor. 1 = Temp. sensor , 2 = Temp + Humid sensor , 3 = Door sensor , 4 = Airflow Sensor ( reserved ) , 5 = Smoke Sensor
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.5.[1..16].[1..2] | THSensorConnState | Read Only | The connection status of the sensor. 0 = disconnected , 1 = connected
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.6.[1..16].[1..2] | THSensorAlarmState | Read Only | The alarm state of the sensor. For Temp sensor : 0 = normal , 10 = Temp. alarm For TH sensor : 0 = normal , 10 = Temp alarm , 11 = Temp & Humid alarm For Door sensor : 0 = Door close , 1 = Door open For Airflow sensor : 0 = normal , 1 = Airflow alarm For Smoke sensor : 0 = normal , 1 = Smoke alarm
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.7.[1..16].[1..2] | tempSensorValue | Read Only | For Temp or TH sensor : The temp. measured in tenth of Degree Celsius 0 = 0C , 10 = 1C , 123 = 12.3C , 999 = 99.9C For door sensor : The door status 48 = door open , 49 = door close For Airflow sensor : The airflow volume flow rate measured in tenth of cubic feet per minute ( CFM ) 0 = 0 cfm , 10 = 1cfm , 123 = 12.3 cfm For Smoke sensor : The smoke sensor status 48 = Smoke alarm , 49 = Smoke normal
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.8.[1..16].[1..2] | tempSensorValueStr | Read Only | For Temp or TH sensor : The temp. measured in tenth of Degree Celsius ---- = disconnected , 0000 = 0C , 0010 = 1C , 0123 = 12.3C , 0999 = 99.9C For door sensor : The door status 0048 = door open , 0049 = door close For Airflow sensor : The airflow volume flow rate measured in tenth of cubic feet per minute ( CFM ) 0000 = 0 cfm , 0010 = 1cfm , 0123 = 12.3 cfm For Smoke sensor : The smoke sensor status 0048 = Smoke alarm , 0049 = Smoke normal
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.9.[1..16].[1..2] | tempSensorUpperAlarmThresh | Read / Write | The temp. alarm threshold in tenth of Degree Celsius Set : 0000 = 0C , 0010 = 1C , 0123 = 12.3C , 0999 =99.9C
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.10.[1..16].[1..2] | tempSensorLowerAlarmThresh | Read Only | The temp. alarm threshold in tenth of Degree Celsius 0000 = 0C , 0010 = 1C , 0123 = 12.3C , 0999 =99.9C
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.11.[1..16].[1..2] | humiSensorValue | Read Only | The relative humidity measured in tenth of percentage. 0 = 0% , 1 = 0.1% , 255 = 25.5% , 999 = 99.9%
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.12.[1..16].[1..2] | humiSensorValueStr | Read Only | The relative humidity measured in tenth of percentage. ---- = disconnected , 000 = 0% , 001 = 0.1% , 025 = 2.5% , 999 = 99.9%
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.13.[1..16].[1..2] | humiSensorUpperAlarmThresh | Read / Write | The relative humidity alarm threshold in tenth of percentage Set : 000 = 0% , 001 = 0.1% , 025 = 2.5% , 999 = 99.9%
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.14.[1..16].[1..2] | humiSensorLowerAlarmThresh | Read Only | The relative humidity alarm threshold in tenth of percentage 000 = 0% , 001 = 0.1% , 025 = 2.5% , 999 = 99.9%
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.15.[1..16].[1..2] | THSensorActivation | Read / Write | The activation state of the sensor Set : 0 = deactivated , 1 = activated
.1.3.6.1.4.1.34550.20.2.1.1.1.28 | rCMSensors | N/A
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1 | rCMSensorTable | N/A | Table of RCM Sensor
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1 | rCMSensorTableEntry | N/A | Table entries of RCM Sensor
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.1 | rCMSensorIndex | Read Only | The ID of RCM sensors. From 1 ~ 13, 1 = RCM 1 , 13 = RCM 13
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.2 | rCMSensorLocation | Read / Write | The location of RCM sensor. Range : 1 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.3 | rCMSensorReading | Read Only | The reading of RCM in tenth of mA
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.4 | rCMSensorConnState | Read Only | The connection status of the sensor. 0 = disconnected , 1 = connected
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.5 | rCMSensorAlarmState | Read Only | The alarm state of the RCM sensor. 0 = normal , 1 = alarm , 2 = rising alert
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.6 | rCMSensorAlarmThreh | Read / Write | To set the RCM alarm threshold in tenth mA. 10 = 1.0mA , 100 = 10.0mA
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.7 | rCMSensorRisingAlertThreh | Read / Write | To set the RCM rising alert threshold in tenth mA. 10 = 1.0mA , 100 = 10.0mA
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.8 | rCMSensorLowAlertThreh | Read / Write | Reserved
.1.3.6.1.4.1.34550.20.2.2 | pduTraps | N/A
.1.3.6.1.4.1.34550.20.2.2.1 | circuitLoadEventTriggered | N/A | By default, a trap will send out in cycle when the circuit / bank level current load over the circuit amp. alarm threshold. It will stop when the cirucit level current load is below the circuit amp. alarm threshold. The time interval for one cycle is within 3 mins if 16 PDUs are connected.
.1.3.6.1.4.1.34550.20.2.2.2 | circuitLoadEventCleared | N/A | By default, a trap will send out once when the circuit / bank level current load resume normal.
.1.3.6.1.4.1.34550.20.2.2.12 | circuitBreakerTripped | N/A | By default, a trap will send out in cycle when the circuit breaker is tripped. The time interval for one cycle is within 3 mins if 16 PDUs are connected.
.1.3.6.1.4.1.34550.20.2.2.13 | circuitBreakerRecovered | N/A | By default, a trap will send out once when the circuit breaker is resumed normal.
.1.3.6.1.4.1.34550.20.2.2.39 | sensorConnectionRecovered | N/A | By default , a trap will send out once when the sensor is reconnected.
.1.3.6.1.4.1.34550.20.2.2.40 | sensorConnectionLost | N/A | By default, a trap will send out in cycle when sensor ( Temp. / TH / Door / Airflow or Smoke ) is disconnected. It will stop when the sensor is reconnected. The time interval for one cycle is within 3 mins if 16 PDUs are connected.
.1.3.6.1.4.1.34550.20.2.2.41 | tempSesnorEventTriggered | N/A | By default, a trap will send out in cycle when the temp. reading is over the temp. alarm threshold. It will stop when the temp. reading is below the temp. alarm threshold. The time interval for one cycle is within 3 mins if 16 PDUs are connected.
.1.3.6.1.4.1.34550.20.2.2.42 | tempSesnorEventCleared | N/A | By default, a trap will send out once when the temp. reading resumes normal.
.1.3.6.1.4.1.34550.20.2.2.47 | humiSensorEventTriggered | N/A | By default, a trap will send out in cycle when the relative humid. reading is over the humid. alarm threshold. It will stop when the relative humid. reading is below the humid. alarm threshold. The time interval for one cycle is within 3 mins if 16 PDUs are connected.
.1.3.6.1.4.1.34550.20.2.2.48 | humiSensorEventCleared | N/A | By default, a trap will send out once when the humid reading resumes normal.
.1.3.6.1.4.1.34550.20.2.2.53 | pduConnectionLost | N/A | By default, a trap will send out in cycle when the PDU is disconnected. It will stop when the PDU is reconnected. The time interval for one cycle is within 3 mins if 16 PDUs are connected.
.1.3.6.1.4.1.34550.20.2.2.54 | pduConnectionRecovered | N/A | By default, a trap will send out once when the PDU is reconnected.
.1.3.6.1.4.1.34550.20.2.2.61 | doorSensorEventTriggered | N/A | By default, a trap will send out once when the door sensor is opened. The time interval for one cycle is within 3 mins if 16 PDUs are connected
.1.3.6.1.4.1.34550.20.2.2.62 | doorSensorEventCleared | N/A | By default, a trap will send out once when the door sensor is closed.
.1.3.6.1.4.1.34550.20.2.2.63 | smokeSensorEventTriggered | N/A | By default, a trap will send out in cycle when the smoke is in alarm state. The time interval for one cycle is within 3 mins if 16 PDUs are connected.
.1.3.6.1.4.1.34550.20.2.2.64 | smokeSensorEventCleared | N/A | By default, a trap will send out once whan the smoke sensor resumes normal.
.1.3.6.1.4.1.34550.20.2.2.80 | rcmSensorEventTriggered | N/A | By default, a trap will send out in cycle when RCM reading is over the RCM alarm threshold.
.1.3.6.1.4.1.34550.20.2.2.81 | rcmSensorEventCleared | N/A | By default, a trap will send out once when RCM reading returns below the RCM alarm threshold.
.1.3.6.1.4.1.34550.20.2.2.82 | rcmSensorConnectionLost | N/A | By default, a trap will send out in cycle when RCM sensor loses communication.
.1.3.6.1.4.1.34550.20.2.2.83 | rcmSensorConnectionRecovered | N/A | By default, a trap will send out once when RCM sensor resumes communication
.1.3.6.1.4.1.34550.20.4 | atsGroup | N/A | N/A
.1.3.6.1.4.1.34550.20.4.1 | atsAdmin | N/A | N/A
.1.3.6.1.4.1.34550.20.4.1.1 | atsTable | N/A | Table of ATS
.1.3.6.1.4.1.34550.20.4.1.1.1 | atsEntry | N/A | Table Entries of ATS
.1.3.6.1.4.1.34550.20.4.1.1.1.1.[16] | atsIndex | Read Only | ATS level
.1.3.6.1.4.1.34550.20.4.1.1.1.2.[16] | atsModel | Read Only | ATS Model no.
.1.3.6.1.4.1.34550.20.4.1.1.1.3.[16] | atsID | Read Only | ATS unique identifier
.1.3.6.1.4.1.34550.20.4.1.1.1.4.[16] | atsName | Read / Write | The name of ATS. Length : 1 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.4.1.1.1.5.[16] | atsLocation | Read / Write | The name of Location. Length : 1 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.4.1.1.1.6.[16] | atsInputSwitch | Read / Write | The selection of preferred source. 0 = Primary , 1 = Secondary Set : 0 = Primary , 1 = Secondary
.1.3.6.1.4.1.34550.20.4.1.1.1.7.[16] | atsFeedPrimaryStatus | Read Only | The status of Primary source. 0 = offine , 1 = online
.1.3.6.1.4.1.34550.20.4.1.1.1.8.[16] | atsFeedSecondaryStatus | Read Only | The status of Secondary source. 0 = offine , 1 = online
.1.3.6.1.4.1.34550.20.4.1.1.1.9.[16] | atsOutputFromFeed | Read Only | To show which source are supplying the electricity. 0 = Primary , 1 = Secondary
.1.3.6.1.4.1.34550.20.4.1.1.1.10.[16] | atsTotalLoadAmp | Read Only | The total current loading of the ATS in tenth of amp. 0 = 0.0A , 999 = 99.9A
.1.3.6.1.4.1.34550.20.4.1.1.1.11.[16] | atsOverLoadThreshold | Read Only | The Overload threshold of the ATS which equals to the rated input ampere. 0 = 0.0A , 999 = 99.9A The value of the overload threshold equals to 90% of the rated input ampere.
.1.3.6.1.4.1.34550.20.4.1.1.1.12.[16] | atsOverLoadStage | Read Only | The Overload stage of ATS. 0 = normal , 1 = alarm ( over the overload threshold )
.1.3.6.1.4.1.34550.20.4.1.1.1.13.[16] | atsConnection | Read Only | The connection status of ATS. 0 = disconnected , 1 = connected
.1.3.6.1.4.1.34550.20.4.2 | atsTraps | N/A
.1.3.6.1.4.1.34550.20.4.2.1 | atsOverLoadEventTriggered | N/A | A trap will send out continuously when current loading of the ATS is over the overload threshold. It will stop when the current loading is below the overload threshold.
.1.3.6.1.4.1.34550.20.4.2.2 | atsOverLoadEventCleared | N/A | A trap will send out once when the current loading returns to the value below the overload threshold.
.1.3.6.1.4.1.34550.20.4.2.3 | atsPrimaryFeedOfflineEventTriggered | N/A | A trap will send out continuously when the Primary source is offline. It will stop when the Primary source is resume normal.
.1.3.6.1.4.1.34550.20.4.2.4 | atsPrimaryFeedOfflineEventCleared | N/A | A trap will send out once when the Primary source is resume.
.1.3.6.1.4.1.34550.20.4.2.5 | atsSecondaryFeedOfflineEventTriggered | N/A | A trap will send out continuously when the Secondary source is offline. It will stop when the Secondary source is resume normal.
.1.3.6.1.4.1.34550.20.4.2.6 | atsSecondaryFeedOfflineEventCleared | N/A | A trap will send out once when the Secondary source is resume.
.1.3.6.1.4.1.34550.20.4.2.7 | atsInputSwitchEventTriggered | N/A | A trap will send out once when the preferred source is changed.
.1.3.6.1.4.1.34550.20.4.2.8 | atsOnFailAutoSwitchFeedEventTriggered | N/A | A trap will send out once when the preferred source is offline.
.1.3.6.1.4.1.34550.20.4.2.9 | atsConnectionLost | N/A | A trap will send out continuously when the ATS communication is lost. It will stop when the ATS communicatoin is resume.
.1.3.6.1.4.1.34550.20.4.2.10 | astConnectionRecovered | N/A | A trap will send out once when the ATS communication is resume.