## InfraCool
OID | Name | Access Type | Description
.1.3.6.1.4.1.34550.40 | InfraCool | N/A | N/A
.1.3.6.1.4.1.34550.40.1 | ipMasterFanUnit | N/A | N/A
.1.3.6.1.4.1.34550.40.1.1 | ipMasterFanUnitAdmin | N/A | N/A
.1.3.6.1.4.1.34550.40.1.1.1.0 | ipmasterFanUnitModel | Read Only | InfraCool
.1.3.6.1.4.1.34550.40.1.1.5.0 | ipmasterFanUnitName | Read / Write | The name of the Master IP Fan Unit Length : 1 to 16 char. Valid char. : " 0 ~ 9 ", " a ~ z ", " A ~ Z ", " _ ", " - " & " . ".
.1.3.6.1.4.1.34550.40.1.1.6.0 | ipmasterFanUnitLocation | Read / Write | The location of the Master IP Fan Unit Length : 1 to 16 char. Valid char. : " 0 ~ 9 ", " a ~ z ", " A ~ Z ", " _ ", " - " & " . ".
.1.3.6.1.4.1.34550.40.1.1.8.0 | ipmasterFanUnitMacAddress | Read Only | The MAC address of the Master IP Fan
.1.3.6.1.4.1.34550.40.1.1.9.0 | ipmasterFanUnitIpAddressIpv4 | Read Only | The IPv4 address of the Master IP Fan
.1.3.6.1.4.1.34550.40.1.1.10.0 | ipmasterFanUnitSubnetIpv4 | Read Only | The IPv4 subnet of the Master IP Fan
.1.3.6.1.4.1.34550.40.1.1.11.0 | ipmasterFanUnitGatewayIpv4 | Read Only | The IPv4 gateway of the Master IP Fan
.1.3.6.1.4.1.34550.40.2 | fanUnitGroup | N/A | N/A
.1.3.6.1.4.1.34550.40.2.1 | fanUnitAdmin | N/A | N/A
.1.3.6.1.4.1.34550.40.2.1.1 | fanUnitTable | N/A | Table of fan unit
.1.3.6.1.4.1.34550.40.2.1.1.1 | fanUnitEntry | N/A | Table Entries of fan unit
.1.3.6.1.4.1.34550.40.2.1.1.1.1.[1..16] | fanunitIndex | Read Only | fan unit level in the Group , Level : 1 to 16 .1.3.6.1.4.1.34550.40.2.1.1.1.1.1 = fan unit level 1 .1.3.6.1.4.1.34550.40.2.1.1.1.1.16 = fan unit level 16
.1.3.6.1.4.1.34550.40.2.1.1.1.2.[1..16] | fanUnitModel | Read Only | fan unit model No. , Level : 1 to 16 .1.3.6.1.4.1.34550.40.2.1.1.1.2.1 = fan unit level 1 .1.3.6.1.4.1.34550.40.2.1.1.1.2.16 = fan unit level 16
.1.3.6.1.4.1.34550.40.2.1.1.1.3.[1..16] | fanUnitID | Read Only | fan unit unique identifier , Level : 1 to 16 .1.3.6.1.4.1.34550.40.2.1.1.1.3.1 = fan unit level 1 .1.3.6.1.4.1.34550.40.2.1.1.1.3.16 = fan unit level 1
.1.3.6.1.4.1.34550.40.2.1.1.1.4.[1..16] | fanUnitRack | Read / Write | The rack name where the fan unit is installed , Level : 1 to 16 Length : 1 to 16 char. Valid char. : " 0 ~ 9 ", " a ~ z ", " A ~ Z ", " _ ", " - " & " . ". If less than 16 char. , the remaining char. will be filled by " _ "
.1.3.6.1.4.1.34550.40.2.1.1.1.5.[1..16] | fanUnitPosition | Read / Write | The Location of fan unit in rack , Level : 1 to 16 Length : 1 to 16 char. Valid char. : " 0 ~ 9 ", " a ~ z ", " A ~ Z ", " _ ", " - " & " . ". If less than 16 char. , the remaining char. will be filled by " _ "
.1.3.6.1.4.1.34550.40.2.1.1.1.6.[1..16] | fanUnitFirmware | Read Only | The Firmware version of the Fan unit's control panel, Level : 1 to 16 .1.3.6.1.4.1.34550.40.2.1.1.1.6.1 = Fan level 1 .1.3.6.1.4.1.34550.40.2.1.1.1.6.16 = Fan level 16
.1.3.6.1.4.1.34550.40.2.1.1.1.7.[1..16] | fanUnitTotalNoOfFanKits | Read Only | The no of fan kit of each fan unit, Level : 1 to 16 .1.3.6.1.4.1.34550.40.2.1.1.1.7.1 = Fan level 1 .1.3.6.1.4.1.34550.40.2.1.1.1.7.16 = Fan level 16
.1.3.6.1.4.1.34550.40.2.1.1.1.8.[1..16] | fanUnitCFMsetting | Read / Write | The CFM setting of the Fan, Level : 1 to 16 .1.3.6.1.4.1.34550.40.2.1.1.1.8.1 = Fan level 1 .1.3.6.1.4.1.34550.40.2.1.1.1.8.16 = Fan level 16 Set : 1= Normal , 2= High , 3 = Max
.1.3.6.1.4.1.34550.40.2.1.1.1.9.[1..16] | fanUnitConnection | Read Only | The connection status of the fan unit. 0 = disconnected , 1 = connected
.1.3.6.1.4.1.34550.40.2.1.1.1.10.[1..16] | fanUnitStatus | Read Only | The status of the fan unit. 0 = Normal , 1 = Alarm
.1.3.6.1.4.1.34550.40.2.1.1.1.11.[1..16] | fanUnitSpeed | Read Only | The speed of the fan unit. 0 = Off , 1 = Normal , 2 = High , 3 = Max
.1.3.6.1.4.1.34550.40.2.1.1.1.12.[1..16] | fanUnitSwitch | Read / Write | To switch ON / OFF the fan unit. Set : 0 = Off , 1 = On
.1.3.6.1.4.1.34550.40.2.1.1.1.20.[1..16] | TempSensorActivation | Read / Write | To activate / deactivate of the temp. sensor of fan unit Set :0 = deactivate , 1 = activate
.1.3.6.1.4.1.34550.40.2.1.1.1.21.[1..16] | TempSensorLocation | Read / Write | The location of temp. sensor of the fan unit, Level : 1 to 16 Length : 1 to 16 char. Valid char. : " 0 ~ 9 ", " a ~ z ", " A ~ Z ", " _ ", " - " & " . ". If less than 16 char. , the remaining char. will be filled by " _ "
.1.3.6.1.4.1.34550.40.2.1.1.1.22.[1..16] | TempSensorAutoCFMControl | Read / Write | The auto CFM control setting of the fan unit. Set : 0 = disable , 1 = enable
.1.3.6.1.4.1.34550.40.2.1.1.1.23.[1..16] | TempSensorUpperAlarmThreshold | Read / Write | The alarm threshold of the temp. sensor Set : 0000 = 0 degree C , 0999 = 99.9 degree C
.1.3.6.1.4.1.34550.40.2.1.1.1.24.[1..16] | TempSensorRisingAlertThreshold | Read / Write | The rising alert threshold of the temp. sensor Set : 0000 = 0 degree C , 0999 = 99.9 degree C
.1.3.6.1.4.1.34550.40.2.1.1.1.25.[1..16] | TempSensorReadingC | Read Only | The temperature reading of the temp. sensor in degree C 0000 = 0 degree C , 0999 = 99.9 degree C
.1.3.6.1.4.1.34550.40.2.1.1.1.26.[1..16] | TempSensorStatus | Read Only | The status of the temp. sensor. 0 = Normal , 1 = Alarm , 2 = Rising alert
.1.3.6.1.4.1.34550.40.2.1.1.1.30.[1..16] | fanKitConnectionStr | Read Only | The connecttion state of the fan kits. From 00000000000000000000 to 11111111111111111111 For MRF1.6 / RF 1.6 = 00000000000111000111 For MRF 1.9 / RF 1.9 = 00000000000111111111
.1.3.6.1.4.1.34550.40.2.1.1.1.31.[1..16] | fanKitSpeedStr | Read Only | The speed of the fan kits. From 00000000000000000000 to 33333333333333333333 For MRF1.3 / RF 1.3 in High speed = 00000000000000000111 For MRF1.6 / RF 1.6 in Normal speed = 00000000000111000111 For MRF 1.9 / RF 1.9 in Max speed = 00000000000333333333
.1.3.6.1.4.1.34550.40.2.1.1.1.32.[1..16] | fanKitStatusStr | Read Only | The status of the all fan kits of the fan unit. 0 = normal , 1, 2, 3 = alarm From 00000000000000000000 to 33333333333333333333 For MRF1.3 / RF 1.3 in alarm state = 00000000000000000111 / 00000000000000000222 / 00000000000000000333 For MRF1.6 / RF 1.6 in alarm state = 00000000000111000111 / 00000000000222000222 / 00000000000333000333 For MRF 1.9 / RF 1.9 in normal state = 00000000000000000000
.1.3.6.1.4.1.34550.40.2.2 | FanTraps | N/A
.1.3.6.1.4.1.34550.40.2.2.1 | fanUnitEventTriggered | N/A | A trap will send out in cycle when the Fan unit in alarm ( When the temp. reading is higher than the temp alarm threshold and the temp. reading can be return to the temp. alarm threshold MINUS 2 degree C in 10 mins ). It will stop when the Fan unit resumes normal. The time interval for one cycle is within 3 mins if 16 Fan units are connected.
.1.3.6.1.4.1.34550.40.2.2.2 | fanUnitEventCleared | N/A | A trap will send out ONCE when the Fan unit returns to normal ( After the temp. reading returns to temp. alarm threshold MINUS 2 degree C ).
.1.3.6.1.4.1.34550.40.2.2.31 | tempSesnorEventTriggered | N/A | A trap will send out in cycle when the temp. reading is over the temp. alarm threshold. It will stop when the temp. reading is below the temp. alarm threshold minus 2 degree Celsius. The time interval for one cycle is within 3 mins if 16 Fan units are connected.
.1.3.6.1.4.1.34550.40.2.2.32 | tempSesnorEventCleared | N/A | A trap will send out ONCE when the temp. reading returns to normal ( Below the temp. alarm threshold )
.1.3.6.1.4.1.34550.40.2.2.51 | fanUnitConnectionLost | N/A | A trap will send out in cycle when the Fan unit is disconnected. It will stop when the Fan units is reconnected. The time interval for one cycle is within 3 mins if 16 Fan units are connected.
.1.3.6.1.4.1.34550.40.2.2.52 | fanUnitConnectionRecovered | N/A | A trap will send out ONCe when the Fan unit is reconnected.
.1.3.6.1.4.1.34550.40.2.2.53 | tempSensorConnectionLost | N/A | A trap will send out in cycle when the Temp. sensor is disconnected. It will stop when the Temp. sensor is reconnected. The time interval for one cycle is within 3 mins if 16 Fan units are connected.
.1.3.6.1.4.1.34550.40.2.2.54 | tempSensorConnectionRecovered | N/A | A trap will send out ONCE when the temp. sensor is reconnected