## InfraPower
OID | Name | Access Type | Description
.1.3.6.1.4.1.34550.20 | InfraPower | N/A | N/A
.1.3.6.1.4.1.34550.20.1 | ipDongle | N/A | N/A
.1.3.6.1.4.1.34550.20.1.1 | ipDongleAdmin | N/A | N/A
.1.3.6.1.4.1.34550.20.1.1.1.0 | ipdongleModel | Read Only | InfraPower
.1.3.6.1.4.1.34550.20.1.1.5.0 | ipdongleName | Read / Write | The name of the IP Dongle Length : 4 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.1.1.6.0 | ipdongleLocation | Read / Write | The Location of the IP Dongle Length : 4 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.1.1.8.0 | ipdongleMacAddress | Read Only | The MAC address of the IP Dongle
.1.3.6.1.4.1.34550.20.1.1.9.0 | ipdongleIpAddressIpv4 | Read Only | The IPv4 address of the IP Dongle
.1.3.6.1.4.1.34550.20.1.1.10.0 | ipdongleSubnetIpv4 | Read Only | The IPv4 subnet of the IP Dongle
.1.3.6.1.4.1.34550.20.1.1.11.0 | ipdongleGatewayIpv4 | Read Only | The IPv4 gateway of the IP Dongle
.1.3.6.1.4.1.34550.20.1.2 | ipDongleWebAccess | N/A | N/A
.1.3.6.1.4.1.34550.20.1.2.1.0 | objectDateTime | accessible for notify | Date & Time of a Trap is triggered
.1.3.6.1.4.1.34550.20.1.2.2.0 | userName | accessible for notify | User name to login the IP Dongle WEBUI
.1.3.6.1.4.1.34550.20.1.2.3.0 | webAccessIpAddress | accessible for notify | IP address of the PC login in the IP Dongle
.1.3.6.1.4.1.34450.20.1.3 | WebLoginTraps | N/A | N/A
.1.3.6.1.4.1.34450.20.1.3.1 | webLogin | N/A | The trap will send out once when user login the IP Dongle
.1.3.6.1.4.1.34550.20.2 | pduGroup | N/A | N/A
.1.3.6.1.4.1.34550.20.2.1 | pduAdmin | N/A | N/A
.1.3.6.1.4.1.34550.20.2.1.1 | pduTable | N/A | Table of PDU
.1.3.6.1.4.1.34550.20.2.1.1.1 | pduEntry | N/A | Table Entries of PDU
.1.3.6.1.4.1.34550.20.2.1.1.1.1.[1..32] | pduIndex | Read Only | PDU level in the Group , Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.1.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.1.32 = PDU level 32
.1.3.6.1.4.1.34550.20.2.1.1.1.2.[1..32] | pduModel | Read Only | PDU model No. , Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.2.1 = PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.2.32 = PDU level 32
.1.3.6.1.4.1.34550.20.2.1.1.1.3.[1..32] | pduID | Read Only | PDU unique identifier , Level : 1 to 32 .1.3.6.1.4.1.34450.20.2.1.1.1.3.1 = PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.3.32 = PDU level 32
.1.3.6.1.4.1.34550.20.2.1.1.1.4.[1..32] | pduSerialNo | Read Only | Serial no. of PDU shown on the W meter with 2.8" color LCD ONLY , Level : 1 to 32 .1.3.6.1.4.1.34450.20.2.1.1.1.3.1 = PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.3.32 = PDU level 32
.1.3.6.1.4.1.34550.20.2.1.1.1.6.[1..32] | pduName | Read / Write | The name of PDU , Level : 1 to 32 Length : 1 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . ) Level : 1 to 32 .1.3.6.1.4.1.34450.20.2.1.1.1.6.1 = PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.6.32 = PDU level 32
.1.3.6.1.4.1.34550.20.2.1.1.1.7.[1..32] | pduLocation | Read / Write | The Location of PDU , Level : 1 to 32 Length : 1 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . ) Level : 1 to 32 .1.3.6.1.4.1.34450.20.2.1.1.1.7.1 = PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.7.32 = PDU level 32
.1.3.6.1.4.1.34550.20.2.1.1.1.8.[1..32] | pduGroupNumber | Ready Only | The number indicates the IP Dongle group the PDU belongs to when using InfraPower Management Software. Group number : from 000 to 240
.1.3.6.1.4.1.34550.20.2.1.1.1.13.[1..32] | pduMainLoadVoltage | Read Only | The voltage measured of the PDU in tenth of Volts , Level : 1 to 32 .1.3.6.1.4.1.34450.20.2.1.1.1.13.1 = PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.13.32 = PDU level 32 Single Phase PDU : 2215 = 221.5 VAC 3 Phase PDU : 2204 ( 2201 , 2205 , 2206 ) = 1st 4 digit is the average voltage of all the phase. The figure in the bracket is the voltage of phase 1 , phase 2 & phase 3 respectively For Dual Feed PDU : voltage = average of Feed I & Feed II of the PDU
.1.3.6.1.4.1.34550.20.2.1.1.1.14.[1..32] | pduMainLoadAmp | Read Only | The current load ampere of the PDU measured in tenth of amp. 0 = 0.0A , 1 = 0.1A , 135 = 13.5A Level : 1 to 32 .1.3.6.1.4.1.34450.20.2.1.1.1.14.1 = PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.14.32 = PDU level 32 For Dual Feed PDU : current loading = sum of current loading of Feed I & Feed II of the PDU
.1.3.6.1.4.1.34550.20.2.1.1.1.16.[1..32] | pduMainPowerFactor | Read Only | The power factor of the PDU measured in hundredth 000 = 0 , 001 = 0.01 , 055 = 0.55 , 100 = 1.0 Level : 1 to 32 .1.3.6.1.4.1.34450.20.2.1.1.1.16.1 = PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.16.32 = PDU level 32 For Dual Feed PDU : Power Factor = average of power factor of Feed I & Feed II of the PDU
.1.3.6.1.4.1.34550.20.2.1.1.1.17.[1..32] | pduMainActivePower | Read Only | The power consumption of the PDU measured in hundred-thousandth of kW Range : 0000000 to 9999999 0 = 0kW , 25 = 0.00025kW , 123 = 0.00123kW , 1234567 = 12.34567kW Level : 1 to 32 .1.3.6.1.4.1.34450.20.2.1.1.1.17.1 = PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.17.32 = PDU level 32 For Dual Feed PDU : Active power = sum of active power of Feed I & Feed II of the PDU
.1.3.6.1.4.1.34550.20.2.1.1.1.18.[1..32] | pduMainApparentPower | Read Only | The power consumption of the PDU measured in hundred-thousandth of kVA Range : 0000000 to 9999999 0 = 0VA , 25 = 0.25VA, 123 = 1.23VA , 1234567 = 12345.67VA Level : 1 to 32 .1.3.6.1.4.1.34450.20.2.1.1.1.18.1 = PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.18.32 = PDU level 32 For Dual Feed PDU : Apparent power = sum of apparent power of Feed I & Feed II of the PDU
.1.3.6.1.4.1.34550.20.2.1.1.1.19.[1..32] | pduMainCumulativeEnergy | Read Only | The accumulated energy consumption of the PDU in hundredth of kWh Range : 00000000 to 99999999 0 = 0.00kWh , 123 = 1.23kWh , 12345 = 123.45kWh , 12345678 = 123456.78kWh Single Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34450.20.2.1.1.1.19.1 = PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.19.32 = PDU level 32 For Dual Feed PDU : Cumulative energy = sum of cumulative energy of Feed I & Feed II of the PDU
.1.3.6.1.4.1.34550.20.2.1.1.1.20.[1..32] | pduRealClock | Read Only | The real time of the PDU. Format : YYMMDDHHNNSSW 1503281759596 = 2015-Mar-28 17:59:59 Saturaday
.1.3.6.1.4.1.34550.20.2.1.1.1.24 | circuits | N/A
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1 | circuitTable | N/A | Table of circuits / banks
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1 | circuitTablEntry | N/A | Table entries of circuit / bank
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.1.[1..32].[1..6] | circuitIndex | Read Only | The ID of the PDU's circuit / bank Single Feed PDU : Single Phase : 1 = Circuit A , 2= Circuit B 63A Single Phase : 1 = bank 1 , 2 = bank 2 , 3 = bank 3 , 4 = bank 4 3 Phase : 1 = bank 1 , 2 = bank 2 , 3 = bank 3 , 4 = bank 4, 5 = bank 5 , 6 = bank 6 Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.1.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.1.16.2 = circuit A of Feed 2 of PDU level 16 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.1.32.1 = circuit A of Feed 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.1.32.4 = circuit B of Feed 2 of PDU level 32 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.1.16.1 = bank 1 of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.1.16.6 = bank 3 of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.2.[1..32].[1..6] | circuitRatedAmp | Read Only | The input current rating of the PDU's circuit / bank in tenth of amp. 100 = 10.0A , 160 = 16.0A , 200 = 20.0A Single Feed PDU : Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.2.16.1 = circuit A of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.2.16.2 = circuit B of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.2.16.1 = Bank 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.2.16.3 = Bank 3 of PDU level 16 3 Phase 6 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.2.16.1 = Bank 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.2.16.6 = Bank 6 of PDU level 16 Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.2.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.2.16.2 = circuit A of Feed 2 of PDU level 16 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.2.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.2.16.2 = circuit B of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.2.16.3 = circuit A of Feed 2 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.2.16.4 = circuit B of Feed 2 of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.2.16.1 = Bank 1 of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.2.16.6 = Bank 3 of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.4.[1..32].[1..6] | circuitName | Read Only | The name of the circuit Single Feed PDU : Single Phase : Circuit A , Circuit B 63A Single Phase : Circuit B1 , Circuit B2 , Circuit B3 , Circuit B4 3 Phase ( 400V ) : L1-B1, L1-B2 , L2-B3, L2-B4, L3-B5, L3-B6 3 Phase ( 208V ) : B1 , B2 , B3 , B4 , B5 , B6 Dual Feed PDU : Single Phase Single Circuit : PDU - I , PDU - II Single Phase Dual Circuit : PDU I - A , PDU I - B , PDU II - A , PDU II - B 3 Phase 3 Bank : 3 Phase ( 400V ) : PDU I - L1-B1, PDU I - L2-B2 , PDU I - L3-B3, PDU II - L1-B1, PDU II - L2-B2 , PDU II - L3-B3, 3 Phase ( 208V ) : PDU I - B1, PDU I - B2 , PDU I - B3, PDU II - B1, PDU II - B2 , PDU II - B3,
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.5.[1..32].[1..6] | circuitState | Read Only | The status of the PDU's circuit / bank. Single Feed PDU : 0 = Normal, 1 = Alarm , 2 = Rising alert , 3 = Low alert , 4 = circuit not exist Single Feed PDU : Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.5.16.1 = circuit A of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.5.16.2 = circuit B of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.5.16.1 = Bank 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.5.16.3 = Bank 3 of PDU level 16 3 Phase 6 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.5.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.5.32.6 = Bank 6 of PDU level 32 Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.5.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.5.16.2 = circuit B of Feed 2 of PDU level 16 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.5.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.5.16.4 = circuit B of Feed 2 of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.5.16.1 = Bank 1 of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.5.16.6 = Bank 3 of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.6.[1..32].[1..6] | circuitLoadVoltage | Read Only | The voltage of the PDU's circuit / bank measured in tenth of volt. 0000 = 0.0VAC , 1100 = 110.0VAC , 2225 = 222.5VAC Single Feed PDU : Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.6.16.1 = circuit A of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.6.16.2 = circuit B of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.6.16.1 = Bank 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.6.16.3 = Bank 3 of PDU level 16 3 Phase 6 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.6.16.1 = Bank 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.6.16.6 = Bank 6 of PDU level 16 Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.6.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.6.16.2 = circuit A of Feed 2 of PDU level 16 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.6.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.6.16.4 = circuit B of Feed 2 of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.6.16.1 = Bank 1 of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.6.16.6 = Bank 3 of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.7.[1..32].[1..6] | circuitLoadAmp | Read Only | The current load ampere of the PDU's circuit / bank measured in tenth of amp. 000 = 0.0A , 001 = 0.01A , 105 = 10.5A Single Feed PDU : Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.7.16.1 = circuit A of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.7.16.2 = circuit B of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.7.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.7.32.3 = Bank 3 of PDU level 32 3 Phase 6 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.7.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.7.32.6 = Bank 6 of PDU level 32 Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.7.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.7.16.2 = circuit A of Feed 2 of PDU level 16 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.7.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.7.16.4 = circuit B of Feed 2 of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.7.32.1 = Bank 1 of Feed 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.7.32.6 = Bank 3 of Feed 2 of PDU level 32
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.9.[1..32].[1..6] | circuitPowerFactor | Read Only | The power factor of the PDU's circuit measured in hundredth 000 = 0 , 001 = 0.01 , 055 = 0.55 , 100 = 1.0 Single Feed PDU : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.9.1.1 = circuit A of PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.9.16.2 = circuit B of PDU level 16 Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.9.1.1 = circuit A of Feed 1 of PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.9.1.2 = circuit A of Feed 2 of PDU level 1 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.9.1.1 = circuit A of Feed 1 of PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.9.1.4 = circuit B of Feed 2 of PDU level 1 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.9.1.1 = Bank 1 of Feed 1 of PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.9.1.6 = Bank 3 of Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.10.[1..32].[1..6] | circuitActivePower | Read Only | The power consumption of the PDU's circuit measured in hundred-thousandth of kW Range : 0000000 to 9999999 0 = 0kW , 25 = 0.00025kW , 123 = 0.00123kW , 1234567 = 12.34567kW Single Feed PDU : Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.10.16.1 = circuit A of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.10.16.2 = circuit B of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.10.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.10.32.3 = Bank 3 of PDU level 32 3 Phase 6 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.10.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.10.32.6 = Bank 6 of PDU level 32 Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.10.1.1 = circuit A of Feed 1 of PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.10.1.2 = circuit A of Feed 2 of PDU level 1 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.10.1.1 = circuit A of Feed 1 of PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.10.1.4 = circuit B of Feed 2 of PDU level 1 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.10.1.1 = Bank 1 of Feed 1 of PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.10.1.6 = Bank 3 of Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.11.[1..32].[1..6] | circuitApparentPower | Read Only | The power consumption of the PDU's circuit measured in hundred-thousandth of kVA Range : 0000000 to 9999999 0 = 0VA , 25 = 0.25VA, 123 = 1.23VA , 1234567 = 12345.67VA Single Feed PDU : Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.11.16.1 = circuit A of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.11.16.2 = circuit B of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.11.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.11.32.3 = Bank 3 of PDU level 32 3 Phase 6 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.11.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.11.32.6 = Bank 6 of PDU level 32 Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.11.1.1 = circuit A of Feed 1 of PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.11.11.2 = circuit A of Feed 2 of PDU level 1 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.11.1.1 = circuit A of Feed 1 of PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.11.1.4 = circuit B of Feed 2 of PDU level 1 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.11.1.1 = Bank 1 of Feed 1 of PDU level 1 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.11.1.6 = Bank 3 of Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.12.[1..32].[1..6] | circuitLoadPeakAmp | Read Only | The peak load ampere of the PDU's circuit / bank recorded in tenth of amp with timestamp. 150330105959@081 = 2015-Mar-30 10:59:59 , 8.1A Single Feed PDU : Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.12.16.1 = circuit A of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.12.16.2 = circuit B of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.12.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.12.32.3 = Bank 3 of PDU level 32 3 Phase 6 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.12.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.12.32.6 = Bank 6 of PDU level 32 Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.12.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.12.16.2 = circuit A of Feed 2 of PDU level 16 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.12.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.12.16.4 = circuit B of Feed 2 of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.12.16.1 = Bank 1 of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.12.16.4 = Bank 3 of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.13.[1..32].[1..6] | circuitCumulativeEnergy | Read Only | The accumulated energy consumption of the PDU's circuit / bank in hundredth of kWh with timestamp Range : 00000000 to 99999999 150330105959@09999999 = 2015-Mar-30 10:59:59 , 99999.99kWh Single Feed PDU : Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.13.16.1 = circuit A of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.13.16.2 = circuit B of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.13.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.13.32.3 = Bank 3 of PDU level 32 3 Phase 6 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.13.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.13.32.6 = Bank 6 of PDU level 32 Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.13.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.13.16.2 = circuit A of Feed 2 of PDU level 16 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.13.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.13.16.4 = circuit B of Feed 2 of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.13.16.1 = Bank 1 of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.13.16.6 = Bank 3 of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.14.[1..32].[1..6] | circuitLoadPeakAmpReset | Read / Write | To reset the PDU's circuit / bank peak amp to zero with timestamp updated. Set : 1 = confirm to reset Single Feed PDU : Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.14.16.1 = circuit A of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.14.16.2 = circuit B of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.14.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.14.32.3 = Bank 3 of PDU level 32 3 Phase 6 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.14.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.14.32.6 = Bank 6 of PDU level 32 Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.14.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.14.16.2 = circuit A of Feed 2 of PDU level 16 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.14.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.14.16.4 = circuit B of Feed 2 of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.14.16.1 = Bank 1 of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.14.16.6 = Bank 3 of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.15.[1..32].[1..6] | circuitBreakerStateCopy | Read Only | The circuit breaker state of the PDU. 0 = normal , 1 = tripped Single Feed PDU : Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.15.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.15.16.2 = circuit A of Feed 2 of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.15.16.1 = Bank 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.15.16.3 = Bank 3 of PDU level 16 3 Phase 6 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.15.16.1 = Bank 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.15.16.6 = Bank 6 of PDU level 16 Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.15.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.15.16.2 = circuit A of Feed 2 of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.15.16.1 = Bank 1 of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.15.16.6 = Bank 3 of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.16.[1..32].[1..6] | circuitLoadAmpAlarmThresh | Read / Write | To set the current load ampere alarm threshold of the PDU's circuit / bank in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A Sinlge Feed PDU : Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.16.16.1 = circuit A of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.16.16.2 = circuit B of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.16.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.16.32.3 = Bank 3 of PDU level 32 3 Phase 6 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.16.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.16.32.6 = Bank 6 of PDU level 32 Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.16.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.16.16.2 = circuit A of Feed 2 of PDU level 16 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.16.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.16.16.4 = circuit B of Feed 2 of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.16.16.1 = Bank 1 of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.16.16.3 = Bank 3 of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.17.[1..32].[1..6] | circuitLoadAmpRisingAlertThresh | Read / Write | To set the current load ampere rising alert threshold of the PDU's circuit / bank in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A Single Feed PDU : Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.17.16.1 = circuit A of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.17.16.2 = circuit B of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.17.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.17.32.3 = Bank 3 of PDU level 32 3 Phase 6 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.17.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.17.32.6 = Bank 6 of PDU level 32 Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.17.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.17.16.2 = circuit A of Feed 2 of PDU level 16 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.17.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.17.16.4 = circuit B of Feed 2 of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.17.16.1 = Bank 1 of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.17.16.6= Bank 3 of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.18.[1..32].[1..6] | circuitLoadAmpLowAlertThresh | Read / Write | To set the current load ampere low alert threshold of the PDU's circuit / bank in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A Dual Feed PDU : Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.18.16.1 = circuit A of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.18.16.2 = circuit B of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.18.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.18.32.3 = Bank 3 of PDU level 32 3 Phase 6 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.18.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.18.32.6 = Bank 6 of PDU level 32 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.18.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.18.16.4 = circuit B of Feed 2 of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.18.16.1 = Bank 1 of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.18.16.6 = Bank 6 of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.19.[1..32].[1..6] | circuitCumulativeEnergyReset | Read / Write | To reset the PDU's circuit / bank cumulative energy to zero with timestamp updated. Set : 1 = confirm to reset Single Feed PDU : Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.19.16.1 = circuit A of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.19.16.2 = circuit B of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.19.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.19.32.3 = Bank 3 of PDU level 32 3 Phase 6 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.19.32.1 = Bank 1 of PDU level 32 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.19.32.6 = Bank 6 of PDU level 32 Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.19.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.19.16.2 = circuit A of Feed 2 of PDU level 16 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.19.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.19.16.4 = circuit B of Feed 2 of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.19.16.1 = Bank 1 of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.24.1.1.19.16.6 = Bank 6 of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.25 | circuitBreakers | N/A
.1.3.6.1.4.1.34550.20.2.1.1.1.25.1 | circuitBreakerTable | N/A | Table of circuit breaker
.1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1 | circuitBreakerTableEntry | N/A | Table entries of circuit breaker
.1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.1.[1..32].[1..6] | circuitBreakerIndex | Read Only | The ID of the PDU's circuit breaker. Single Feed PDU : Single Phase : 1 = circuit A's circuit breaker, 2 = circuit B's circuit breaker 63A Single Phase : 1 = bank 1's circuit breaker , 2 = bank 2's circuit breaker , 3 = bank 3's circuit breaker , 4 = bank 4's circuit breaker 3 Phase : 1 = bank 1's circuit breaker , 2 = bank 2's circuit breaker , 3 = bank 3's circuit breaker , 4 = bank 4's circuit breaker , 5 = bank 5's circuit breaker , 6 = bank 6's circuit breaker Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.1.16.1 = circuit A's circuit breaker of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.1.16.2 = circuit A's circuit breaker of Feed 2 of PDU level 16 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.1.16.1 = circuit A's circuit breaker of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.1.16.4 = circuit B's circuit breaker of Feed 2 of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.1.16.1 = bank 1's circuit breaker of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.1.16.6 = bank 3's circuit breaker of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.2.[1..32].[1..6] | circuitBreakerRatedAmp | Read Only | The current rating of the PDU's circuit breaker in tenth of amp. 100 = 10.0A , 160 = 16.0A , 200 = 20.0A Single Feed PDU : Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.2.16.1 = circuit A of of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.2.16.2 = circuit B of of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.2.16.1 = Bank 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.2.16.3 = Bank 3 of PDU level 16 3 Phase 6 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.2.16.1 = Bank 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.2.16.6 = Bank 6 of PDU level 16 Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.2.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.2.16.2 = circuit A of Feed 2 of PDU level 16 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.2.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.2.16.4 = circuit B of Feed 2 of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.2.16.1 = Bank 1 of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.2.16.6 = Bank 3 of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.4.[1..32].[1..6] | circuitBreakerState | Read Only | The circuit breaker state of the PDU. 0 = normal , 1 = tripped Single Feed PDU : Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.4.16.1 = circuit A's circuit breaker of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.4.16.2 = circuit B's circuit breaker of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.4.16.1 = Bank 1's circuit breaker of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.4.16.3 = Bank 3''s circuit breaker of PDU level 16 3 Phase 6 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.4.16.1 = Bank 1's circuit breaker of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.4.16.6 = Bank 6''s circuit breaker of PDU level 16 Dual Feed PDU : Single Phase Single Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.4.16.1 = circuit A's circuit breaker of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.4.16.2 = circuit A's circuit breaker of Feed 2 of PDU level 16 Single Phase Dual Circuit : .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.4.16.1 = circuit A's circuit breaker of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.4.16.4 = circuit B's circuit breaker of Feed 2 of PDU level 16 3 Phase 3 Bank : .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.4.16.1 = Bank 1's circuit breaker of Feed 1 of PDU level 16 .1.3.6.1.4.1.34450.20.2.1.1.1.25.1.1.4.16.6 = Bank 3''s circuit breaker of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.26 | outlets | N/A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1 | stdOutletTable | N/A | Table of non - C19 outlet
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1 | stdOutletTableEntry | N/A | Table entries of non - C19 outlet
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.1.[1..32].[1..72] | stdOutletIndex | Read Only | The ID of the PDU's non - C19 outlet. Range : 1 to 72. 1 = outlet 01, 72 = outlet 72
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.2.[1..32].[1..72] | stdOutletCircuit | Read Only | The circuit of the outlet belongs to - Single Feed PDU : Single phase : 1 = circuit A , 2 = circuit B 63A single phase : 1 = bank 1 , 2 = bank 2 , 3 = bank , 4 = bank 4 3 Phase : 1 = bank 1 , 2 = bank 2 , 3 = bank , 4 = bank 4 , 5 = bank 5 , 6 = bank 6 Dual Feed PDU : Single phase : 1 = PDU I - A , PDU I - B , PDU II - A , PDU II - B 3 Phase 3 Bank : 1 = PDU I - Bank 1 , 2 = PDU I - Bank 2 , 3 = PDU I - Bank 3 , 4 = PDU II - Bank 1 , 5 = PDU II - Bank 2 , 6 = PDU II - Bank 3
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.3.[1..32].[1..72] | stdOutletType | Read Only | The type of non - C19 outlet. 1 = IEC C13 , 3 = BS1363 , 4 = NEMA 5-204 , 5 = Schuko , 6 = AS 31125 , 7 = French , 8 = 60309-16A , 9 =60309-32A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.4.[1..32].[1..72] | stdOutletName | Read / Write | The name of the outlet. Range : 4 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) , ( . ) and ( space )
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.7.[1..32].[1..72] | stdOutletPowerStatus | Read / Write | The power state of the outlet. 0 = OFF , 1 = ON Set : 0 = switch off , 1 = switch on
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.8.[1..32].[1..72] | stdOutletAlarmState | Read Only | The alarm state of the outlet. 0 = Normal, 1 = Alarm , 2 = Rising alert , 3 = Low alert
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.9.[1..32].[1..72] | stdOutletLoadAmp | Read Only | The current load ampere of the outlet measured in tenth of amp. 000 = 0.0A , 001 = 0.01A , 105 = 10.5A , " --- " = immeasurable
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.10.[1..32].[1..72] | stdOutletEnergy | Read Only | The power consumption of the OUTLET measured in hundred-thousandth of kW. Range : 0000000 to 9999999 0 = 0kW , 25 = 0.00025kW , 123 = 0.00123kW , 1234567 = 12.34567kW
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.11.[1..32].[1..72] | stdOutletPeakAmp | Read Only | The peak load ampere of the outlet recorded in tenth of amp with timestamp. 150330105959@031 = 2015-Mar-30 10:59:59 , 3.1A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.12.[1..32].[1..72] | stdOutletCumulativeEnergy | Read Only | The accumulated energy consumption of the outlet in hundredth of kWh with timestamp Range : 00000000 to 99999999 150330105959@09999999 = 2015-Mar-30 10:59:59 , 99999.99kWh
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.13.[1..32].[1..72] | stdOutletLoadAmpAlarmThresh | Read / Write | To set the current load ampere alarm threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.14.[1..32].[1..72] | stdOutletLoadAmpRisingAlertThresh | Read / Write | To set the current load ampere rising alert threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.15.[1..32].[1..72] | stdOutletLoadAmpLowAlertThresh | Read / Write | To set the current load ampere low alert threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.16.[1..32].[1..72] | stdOutletPeakAmpReset | Read / Write | To reset the outlet peak amp reacord to zero with timestamp updated. Set : 1 = confirm to reset
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.17.[1..32].[1..72] | stdOutletCumulativeEnergyReset | Read / Write | To reset the outlet accumulated energy consumpiton record to zero with timestamp updated. Set : 1 = confirm to reset
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.18.[1..32].[1..72] | stdOutletPowerUpSequenceDelay | Read / Write | To set the sequential power up interval between outlet in second. Range : 1 to 10 sec. Set : 0 = 1 sec , 5 = 6 sec , 9 = 10 sec
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2 | c19OutletTable | N/A | Table of C19 outlet
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1 | c19OutletTableEntry | N/A | Table entries of C19 outlet
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.1.[1..32].[1..72] | c19OutletIndex | Read Only | The ID of the PDU's C19 outlet. Range : 1 to 72. 1 = outlet C01, 72 = outlet C72
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.2.[1..32.[1..72] | c19OutletCircuit | Read Only | The circuit of the outlet belongs to - Single phase : 1 = circuit A , 2 = circuit B 63A single phase : 1 = bank 1 , 2 = bank 2 , 3 = bank , 4 = bank 4 3 Phase : 1 = bank 1 , 2 = bank 2 , 3 = bank , 4 = bank 4 , 5 = bank 5 , 6 = bank 6 Dual Feed PDU : Single phase : 1 = PDU I - A , PDU I - B , PDU II - A , PDU II - B 3 Phase 3 Bank : 1 = PDU I - Bank 1 , 2 = PDU I - Bank 2 , 3 = PDU I - Bank 3 , 4 = PDU II - Bank 1 , 5 = PDU II - Bank 2 , 6 = PDU II - Bank 3
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.3.[1..32].[1..72] | c19OutletType | Read Only | The type of C19 outlet. 2 = IEC C19
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.4.[1..32].[1..72] | c19OutletName | Read / Write | The name of the outlet. Range 4 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) , ( . ) and ( space )
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.7.[1..32].[1..72] | c19OutletPowerStatus | Read / Write | The power state of the outlet. 0 = OFF , 1 = ON Set : 0 = switch off , 1 = switch on
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.8.[1..32].[1..72] | c19OutletAlarmState | Read Only | The alarm state of the outlet. 0 = Normal, 1 = Alarm , 2 = Rising alert , 3 = Low alert
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.9.[1..32].[1..72] | c19OutletLoadAmp | Read Only | The current load ampere of the outlet measured in tenth of amp. 000 = 0.0A , 001 = 0.01A , 105 = 10.5A , " --- " = immeasurable
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.10.[1..32].[1..72] | c19OutletEnergy | Read Only | The power consumption of the OUTLET measured in hundred-thousandth of kW. Range : 0000000 to 9999999 0 = 0kW , 25 = 0.00025kW , 123 = 0.00123kW , 1234567 = 12.34567kW
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.11.[1..32].[1..72] | c19OutletPeakAmp | Read Only | The peak load ampere of the outlet recorded in tenth of amp with timestamp. 150330105959@031 = 2015-Mar-30 10:59:59 , 3.1A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.12.[1..32].[1..72] | c19OutletCumulativeEnergy | Read Only | The accumulated energy consumption of the outlet in hundredth of kWh with timestamp Range : 00000000 to 99999999 150330105959@09999999 = 2015-Mar-30 10:59:59 , 99999.99kWh
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.13.[1..32].[1..72] | c19OutletLoadAmpAlarmThresh | Read / Write | To set the current load ampere alarm threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.14.[1..32].[1..72] | c19OutletLoadAmpRisingAlertThresh | Read / Write | To set the current load ampere rising alert threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.15.[1..32].[1..72] | c19OutletLoadAmpLowAlertThresh | Read / Write | To set the current load ampere low alert threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.16.[1..32].[1..72] | c19OutletPeakAmpReset | Read / Write | To reset the outlet peak amp reacord to zero with timestamp updated. Set : 1 = confirm to reset
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.17.[1..32].[1..72] | c19OutletCumulativeEnergyReset | Read / Write | To reset the outlet accumulated energy consumpiton record to zero with timestamp updated. Set : 1 = confirm to reset
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.18.[1..32].[1..72] | c19OutletPowerUpSequenceDelay | Read / Write | To set the sequential power up interval between outlet in second. Range : 1 to 10 sec. Set : 0 = 1 sec , 5 = 6 sec , 9 = 10 sec
.1.3.6.1.4.1.34550.20.2.1.1.1.27 | THSensors | N/A
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1 | THSensorsTable | N/A | Table of TH sensors
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1 | THSensorsTableEntry | N/A | Table entries of TH sensors
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.1.[1..16].[1..2] | THSensorIndex | Read Only | The ID of TH sensors. 1 = TH 1 , 2 = TH 2
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.3.[1..16].[1..2] | THSensorLocation | Read / Write | The location of TH sensor. Range : 4 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.4.[1..16].[1..2] | THSensorType | Read Only | The type of the sensor. 1 = Temp. sensor , 2 = Temp + Humid sensor , 3 = Door sensor , 4 = Airflow sensor ( reserved ) , 5 = Smoke
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.5.[1..16].[1..2] | THSensorConnState | Read Only | The connection status of the sensor. 0 = disconnected , 1 = connected
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.6.[1..16].[1..2] | THSensorAlarmState | Read Only | The alarm state of the sensor. Temp / TH sensor : 0 = normal , 1 = humid sensor alarm only , 10 = temp. sensor alarm only , 11 = temp + humid sensor alarm Door sensor : 0 = close , 10 = open Airflow sensor : 0 = normal , 10 = alarm ( reserved ) Smoke sensor : 0 = normal , 10 = alarm
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.7.[1..16].[1..2] | tempSensorValue | Read Only | The temp. measured in tenth of Degree Celsius 0 = 0C , 10 = 1C , 123 = 12.3C , 999 = 99.9C
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.8.[1..16].[1..2] | tempSensorValueStr | Read Only | The temp. measured in tenth of Degree Celsius ---- = disconnected , 0000 = 0C , 0010 = 1C , 0123 = 12.3C , 0999 = 99.9C
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.9.[1..16].[1..2] | tempSensorUpperAlarmThresh | Read / Write | The temp. alarm threshold in tenth of Degree Celsius Set : 0000 = 0C , 0010 = 1C , 0123 = 12.3C , 0999 =99.9C
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.10.[1..16].[1..2] | tempSensorLowerAlarmThresh | Read Only | The temp. alarm threshold in tenth of Degree Celsius 0000 = 0C , 0010 = 1C , 0123 = 12.3C , 0999 =99.9C
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.11.[1..16].[1..2] | humiSensorValue | Read Only | The relative humidity measured in tenth of percentage. 0 = 0% , 1 = 0.1% , 255 = 25.5% , 999 = 99.9%
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.12.[1..16].[1..2] | humiSensorValueStr | Read Only | The relative humidity measured in tenth of percentage. ---- = disconnected , 000 = 0% , 001 = 0.1% , 025 = 2.5% , 999 = 99.9%
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.13.[1..16].[1..2] | humiSensorUpperAlarmThresh | Read / Write | The relative humidity alarm threshold in tenth of percentage Set : 000 = 0% , 001 = 0.1% , 025 = 2.5% , 999 = 99.9%
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.14.[1..16].[1..2] | humiSensorLowerAlarmThresh | Read Only | The relative humidity alarm threshold in tenth of percentage 000 = 0% , 001 = 0.1% , 025 = 2.5% , 999 = 99.9%
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.15.[1..16].[1..2] | THSensorActivation | Read / Write | The activation state of the Temp. or Temp. & humid. Sensor. Set : 0 = deactivated , 1 = activated
.1.3.6.1.4.1.34550.20.2.1.1.1.28 | rCMSensors | N/A
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1 | rCMSensorTable | N/A | Table of RCM Sensor
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1 | rCMSensorTableEntry | N/A | Table entries of RCM Sensor
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.1 | rCMSensorIndex | Read Only | The ID of RCM sensors. From 1 ~ 13, 1 = RCM 1 , 13 = RCM 13
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.2 | rCMSensorLocation | Read / Write | The location of RCM sensor. Range : 1 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.3 | rCMSensorReading | Read Only | The reading of RCM in tenth of mA
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.4 | rCMSensorConnState | Read Only | The connection status of the sensor. 0 = disconnected , 1 = connected
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.5 | rCMSensorAlarmState | Read Only | The alarm state of the RCM sensor. 0 = normal , 1 = alarm , 2 = rising alert
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.6 | rCMSensorAlarmThreh | Read / Write | To set the RCM alarm threshold in tenth mA. 10 = 1.0mA , 100 = 10.0mA
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.7 | rCMSensorRisingAlertThreh | Read / Write | To set the RCM rising alert threshold in tenth mA. 10 = 1.0mA , 100 = 10.0mA
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.8 | rCMSensorLowAlertThreh | Read / Write | Reserved
.1.3.6.1.4.1.34550.20.2.2 | pduTraps | N/A
.1.3.6.1.4.1.34450.20.2.2.1 | circuitLoadEventTriggered | N/A | SNMP trap can be disabled, enabled to send out once or in cycle in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.2 | circuitLoadEventCleared | N/A | SNMP trap can be disabled, enabled to send out once in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.12 | circuitBreakerTripped | N/A | SNMP trap can be disabled, enabled to send out once or in cycle in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.13 | circuitBreakerRecovered | N/A | SNMP trap can be disabled, enabled to send out once in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.39 | senosorConnectionRecovered | N/A | SNMP trap can be disabled, enabled to send out once in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.40 | senosorConnectionLost | N/A | SNMP trap can be disabled, enabled to send out once or in cycle in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.41 | tempSesnorEventTriggered | N/A | SNMP trap can be disabled, enabled to send out once or in cycle in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.42 | tempSesnorEventCleared | N/A | SNMP trap can be disabled, enabled to send out once in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.47 | humiSensorEventTriggered | N/A | SNMP trap can be disabled, enabled to send out once or in cycle in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.48 | humiSensorEventCleared | N/A | SNMP trap can be disabled, enabled to send out once in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.53 | pduConnectionLost | N/A | SNMP trap can be disabled, enabled to send out once or in cycle in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.54 | pduConnectionRecovered | N/A | SNMP trap can be disabled, enabled to send out once in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.55 | feedConnectionRecovered | N/A | SNMP trap can be disabled, enabled to send out once in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.56 | feedConnectionLost | N/A | SNMP trap can be disabled, enabled to send out once or in cycle in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.61 | doorSensorEventTriggered | N/A | SNMP trap can be disabled, enabled to send out once or in cycle in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.62 | doorSensorEventCleared | N/A | SNMP trap can be disabled, enabled to send out once in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.63 | smokeSensorEventTriggered | N/A | SNMP trap can be disabled, enabled to send out once or in cycle in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.64 | smokeSensorEventCleared | N/A | SNMP trap can be disabled, enabled to send out once in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.80 | rcmSensorEventTriggered | N/A | SNMP trap can be disabled, enabled to send out once or in cycle in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.81 | rcmSensorEventCleared | N/A | SNMP trap can be disabled, enabled to send out once in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.82 | rcmSensorConnectionLost | N/A | SNMP trap can be disabled, enabled to send out once or in cycle in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34450.20.2.2.83 | rcmSensorConnectionRecovered | N/A | SNMP trap can be disabled, enabled to send out once in SNMP page of IP Dongle WEBUI
.1.3.6.1.4.1.34550.20.4 | atsGroup | N/A | N/A
.1.3.6.1.4.1.34550.20.4.1 | atsAdmin | N/A | N/A
.1.3.6.1.4.1.34550.20.4.1.1 | atsTable | N/A | Table of ATS
.1.3.6.1.4.1.34550.20.4.1.1.1 | atsEntry | N/A | Table Entries of ATS
.1.3.6.1.4.1.34550.20.4.1.1.1.1.[16] | atsIndex | Read Only | ATS level
.1.3.6.1.4.1.34550.20.4.1.1.1.2.[16] | atsModel | Read Only | ATS Model no.
.1.3.6.1.4.1.34550.20.4.1.1.1.3.[16] | atsID | Read Only | ATS unique identifier
.1.3.6.1.4.1.34550.20.4.1.1.1.4.[16] | atsName | Read / Write | The name of ATS. Length : 1 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.4.1.1.1.5.[16] | atsLocation | Read / Write | The name of Location. Length : 1 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.4.1.1.1.6.[16] | atsInputSwitch | Read / Write | The selection of preferred source. 0 = Primary , 1 = Secondary Set : 0 = Primary , 1 = Secondary
.1.3.6.1.4.1.34550.20.4.1.1.1.7.[16] | atsFeedPrimaryStatus | Read Only | The status of Primary source. 0 = offine , 1 = online
.1.3.6.1.4.1.34550.20.4.1.1.1.8.[16] | atsFeedSecondaryStatus | Read Only | The status of Secondary source. 0 = offine , 1 = online
.1.3.6.1.4.1.34550.20.4.1.1.1.9.[16] | atsOutputFromFeed | Read Only | To show which source are supplying the electricity. 0 = Primary , 1 = Secondary
.1.3.6.1.4.1.34550.20.4.1.1.1.10.[16] | atsTotalLoadAmp | Read Only | The total current loading of the ATS in tenth of amp. 0 = 0.0A , 999 = 99.9A
.1.3.6.1.4.1.34550.20.4.1.1.1.11.[16] | atsOverLoadThreshold | Read Only | The Overload threshold of the ATS which equals to the rated input ampere. 0 = 0.0A , 999 = 99.9A The value of the overload threshold equals to 90% of the rated input ampere.
.1.3.6.1.4.1.34550.20.4.1.1.1.12.[16] | atsOverLoadStage | Read Only | The Overload stage of ATS. 0 = normal , 1 = alarm ( over the overload threshold )
.1.3.6.1.4.1.34550.20.4.1.1.1.13.[16] | atsConnection | Read Only | The connection status of ATS. 0 = disconnected , 1 = connected
.1.3.6.1.4.1.34550.20.4.2 | atsTraps | N/A
.1.3.6.1.4.1.34550.20.4.2.1 | atsOverLoadEventTriggered | N/A | A trap will send out continuously when current loading of the ATS is over the overload threshold. It will stop when the current loading is below the overload threshold.
.1.3.6.1.4.1.34550.20.4.2.2 | atsOverLoadEventCleared | N/A | A trap will send out once when the current loading returns to the value below the overload threshold.
.1.3.6.1.4.1.34550.20.4.2.3 | atsPrimaryFeedOfflineEventTriggered | N/A | A trap will send out continuously when the Primary source is offline. It will stop when the Primary source is resume normal.
.1.3.6.1.4.1.34550.20.4.2.4 | atsPrimaryFeedOfflineEventCleared | N/A | A trap will send out once when the Primary source is resume.
.1.3.6.1.4.1.34550.20.4.2.5 | atsSecondaryFeedOfflineEventTriggered | N/A | A trap will send out continuously when the Secondary source is offline. It will stop when the Secondary source is resume normal.
.1.3.6.1.4.1.34550.20.4.2.6 | atsSecondaryFeedOfflineEventCleared | N/A | A trap will send out once when the Secondary source is resume.
.1.3.6.1.4.1.34550.20.4.2.7 | atsInputSwitchEventTriggered | N/A | A trap will send out once when the preferred source is changed.
.1.3.6.1.4.1.34550.20.4.2.8 | atsOnFailAutoSwitchFeedEventTriggered | N/A | A trap will send out once when the preferred source is offline.
.1.3.6.1.4.1.34550.20.4.2.9 | atsConnectionLost | N/A | A trap will send out continuously when the ATS communication is lost. It will stop when the ATS communicatoin is resume.
.1.3.6.1.4.1.34550.20.4.2.10 | astConnectionRecovered | N/A | A trap will send out once when the ATS communication is resume.