## InfraSolution X
OID | Name | Access Type | Description
.1.3.6.1.4.1.34550.10 | InfraSolutionX | N/A | N/A
.1.3.6.1.4.1.34550.10.1 | InfraBox | N/A | N/A
.1.3.6.1.4.1.34550.10.1.1 | InfraBoxAdmin | N/A | N/A
.1.3.6.1.4.1.34550.10.1.1.1.0 | InfraBoxModel | Read Only | Model of InfraBox ( Value = InfraSolution )
.1.3.6.1.4.1.34550.10.1.1.2.0 | InfraBoxName | Read / Write | The name of the InfraBox Length : 1 to 16 char. Space, single quote, double quote, #, %, &, ; and \ are reserved. They will be replaced by " _ "
.1.3.6.1.4.1.34550.10.1.1.3.0 | InfraBoxLocation | Read / Write | The Location of the InfraBox Length : 1 to 16 char. Space, single quote, double quote, #, %, &, ; and \ are reserved. They will be replaced by " _ "
.1.3.6.1.4.1.34550.10.1.1.8.0 | InfraBoxMacAddress | Read Only | The MAC address of the InfraBox
.1.3.6.1.4.1.34550.10.1.1.9.0 | InfraBoxIpAddressIpv4 | Read Only | The IPv4 address of the InfraBox
.1.3.6.1.4.1.34550.10.1.1.10 | InfraBoxSubnetIpv4 | Read Only | The IPv4 subnet of the InfraBox
.1.3.6.1.4.1.34550.10.1.1.11.0 | InfraBoxGatewayIpv4 | Read Only | The IPv4 gateway of the InfraBox
.1.3.6.1.4.1.34550.10.1.1.12.0 | InfraBoxSolutionType | Read Only | 1 = InfraSolution , 2 = InfraGuard , 3 = InfraPower
.1.3.6.1.4.1.34550.10.1.1.13.0 | InfraBoxSolutionFirmwareInformation | Read Only | The firmware version of the InfraBox
.1.3.6.1.4.1.34550.10.2 | handleGroup | N/A | N/A
.1.3.6.1.4.1.34550.10.2.1 | handleAdmin | N/A | N/A
.1.3.6.1.4.1.34550.10.2.1.1 | handleTable | N/A | Table of handle entries
.1.3.6.1.4.1.34550.10.2.1.1.1 | handleEntry | N/A | Entries of handle
.1.3.6.1.4.1.34550.10.2.1.1.1.1.[1..2] | handleIndex | Read Only | The index of this handle , Level : 1 to 2 .1.3.6.1.4.1.34550.10.2.1.1.1.1.1 = front handle .1.3.6.1.4.1.34550.10.2.1.1.1.1.2 = rear handle
.1.3.6.1.4.1.34550.10.2.1.1.1.2.[1..2] | handleModel | Read Only | handle model , Length : 1 to 32 char. The model is fixed to " xHandle_model " .1.3.6.1.4.1.34550.10.2.1.1.1.2.1 = front handle .1.3.6.1.4.1.34550.10.2.1.1.1.2.2 = rear handle
.1.3.6.1.4.1.34550.10.2.1.1.1.4.[1..2] | handleName | Read Only | The name of handle , Length : 1 to 32 char. The name is fixed to " xHandle_name " .1.3.6.1.4.1.34550.10.2.1.1.1.4.1 = front handle .1.3.6.1.4.1.34550.10.2.1.1.1.4.2 = rear handle
.1.3.6.1.4.1.34550.10.2.1.1.1.5.[1..2] | handleBelongToRack | Read Only | The rack which the handle is installed , Length : 1 to 32 char. The name is fixed to " Demo_Rack_A " .1.3.6.1.4.1.34550.10.2.1.1.1.5.1 = front handle .1.3.6.1.4.1.34550.10.2.1.1.1.5.2 = rear handle
.1.3.6.1.4.1.34550.10.2.1.1.1.6.[1..2] | handleBelongToZone | Read Only | The zone where the handle is installed , Length : 1 to 32 char. The name is fixed to " Demo_Zone_A " .1.3.6.1.4.1.34550.10.2.1.1.1.6.1 = front handle .1.3.6.1.4.1.34550.10.2.1.1.1.6.2 = rear handle
.1.3.6.1.4.1.34550.10.2.1.1.1.7.[1..2] | handleLocation | Read Only | Which door the handle is installed , Length : 1 to 32 char. Value = front / rear .1.3.6.1.4.1.34550.10.2.1.1.1.7.1 = front door .1.3.6.1.4.1.34550.10.2.1.1.1.7.2 = rear door
.1.3.6.1.4.1.34550.10.2.1.1.1.8.[1..2] | handleReaderType | Read Only | The reader type of the handle , Length : 1 to 32 char. Value = Proximity / Mifare / iClass .1.3.6.1.4.1.34550.10.2.1.1.1.8.1 = front handle .1.3.6.1.4.1.34550.10.2.1.1.1.8.2 = rear handle
.1.3.6.1.4.1.34550.10.2.1.1.1.11.[1..2] | handleConnectionStatus | Read Only | The connection status of the handle , Length : 1 to 32 char. Status = Connected / Disconnected .1.3.6.1.4.1.34550.10.2.1.1.1.11.1 = front handle .1.3.6.1.4.1.34550.10.2.1.1.1.11.2 = rear handle
.1.3.6.1.4.1.34550.10.2.1.1.1.12.[1..2] | handleLastAccessCardNo | Read Only | The previous card no. which unlock the handle , Length = 8 decimal digital number. Range : 00000001 to 99999999. If the return value is 00000000, it means remote open / key open / unauthorized open
.1.3.6.1.4.1.34550.10.2.1.1.1.13.[1..2] | handleLastOpenTime | Read Only | The previous time stamp of the handle being opened Format : yymmddhhnnss ( 150702134520 = 02-Jul-2015 13:45:20 )
.1.3.6.1.4.1.34550.10.2.1.1.1.14.[1..2] | handleLastCloseTime | Read Only | The previous time stamp of the handle being closed Format : yymmddhhnnss ( 150702144520 = 02-Jul-2015 14:45:20 )
.1.3.6.1.4.1.34550.10.2.1.1.1.15.[1..2] | handleLastAccessDuration | Read Only | The last door open duration Format : ddhhnnss ( e.g. 1d 3h 37m 15s = 27hrs 37mins 15secs )
.1.3.6.1.4.1.34550.10.2.1.1.1.17.[1..2] | handleAlarmState | Read Only | The handle status. Length : 1 char. 0 = normal , 1 = alarm
.1.3.6.1.4.1.34550.10.2.1.1.1.18.[1..2] | handleAccessMode | Read Only | Access mode of handle which indicates the handle lock position. Length = 1 char 0 = key mode ( lock in 9 o'clock position ) , 1 = card mode ( lock in 12 o'clock position )
.1.3.6.1.4.1.34550.10.2.1.1.1.19.[1..2] | handleDoorSensorState | Read Only | The status of door sensor , Length = 1 char. 0 = door close , 1 = door open ( It does not mean the handle is locked or unlocked , please refer to the below OID value for the handle status )
.1.3.6.1.4.1.34550.10.2.1.1.1.20.[1..2] | handleLockState | Read Only | The handle lock status , Length =1. 0 = locked , 1 = unlocked
.1.3.6.1.4.1.34550.10.2.1.5 | handleControl | N/A | N/A
.1.3.6.1.4.1.34550.10.2.1.5.1 | FrontHandleControl | N/A | N/A
.1.3.6.1.4.1.34550.10.2.1.5.1.5 | SetFrontHandleRemoteRelease | Read / Write | Get the handle lock status , Length = 1 char. 0 = locked , 1 = unlocked. Set to remote unlock the handle lock, Length = 1 char. 1 = confirm the remote unlock the handle
.1.3.6.1.4.1.34550.10.2.1.5.2 | RearHandleControl | N/A | N/A
.1.3.6.1.4.1.34550.10.2.1.5.2.5 | SetRearHandleRemoteRelease | Read / Write | Get the handle lock status , Length = 1 char. 0 = locked , 1 = unlocked. Set to remote unlock the handle lock, Length = 1 char. 1 = confirm the remote unlock the handle
.1.3.6.1.4.1.34550.10.2.2 | handleTraps | N/A | N/A
.1.3.6.1.4.1.34550.10.2.2.1 | handleUnlockRemotely | N/A | When handle is unlocked remotely, this trap will send out once.
.1.3.6.1.4.1.34550.10.2.2.2 | handleLocked | N/A | When handle is locked, this trap will send out once.
.1.3.6.1.4.1.34550.10.2.2.3 | doorNormalOpen | N/A | When door is opened normally, this trap will send out once.
.1.3.6.1.4.1.34550.10.2.2.4 | doorClose | N/A | When door is closed, this trap will send out once.
.1.3.6.1.4.1.34550.10.2.2.6 | handleKeyAccess | N/A | When the handle is unlocked by key, this trap will send out once.
.1.3.6.1.4.1.34550.10.2.2.7 | handleAuthorizedCardAccess | N/A | When handle is unlocked by an authorized card, this trap will send out once.
.1.3.6.1.4.1.34550.10.2.2.8 | handleUnauthorizedCard | N/A | When an unauthorized card is present to the handle, this trap will send out once.
.1.3.6.1.4.1.34550.10.2.2.9 | doorAlarmOpem | N/A | When the door is opened unauthorizedly, this trap will send out once.
.1.3.6.1.4.1.34550.10.2.2.12 | doorAlarmStop | N/A | When unauthorized door open alarm is stopped, this trap will send out once.