## InfraSolution X
OID | Name | Access Type | Description
.1.3.6.1.4.1.34550.10 | InfraSolutionX | N/A | N/A
.1.3.6.1.4.1.34550.10.1 | InfraBox | N/A | N/A
.1.3.6.1.4.1.34550.10.1.1 | InfraBoxAdmin | N/A | N/A
.1.3.6.1.4.1.34550.10.1.1.1.0 | InfraBoxModel | Read Only | Model of InfraBox ( Value = InfraSolution )
.1.3.6.1.4.1.34550.10.1.1.2.0 | InfraBoxName | Read / Write | The name of the InfraBox Length : 1 to 16 char. Space, single quote, double quote, #, %, &, ; and \ are reserved. They will be replaced by " _ "
.1.3.6.1.4.1.34550.10.1.1.3.0 | InfraBoxLocation | Read / Write | The Location of the InfraBox Length : 1 to 16 char. Space, single quote, double quote, #, %, &, ; and \ are reserved. They will be replaced by " _ "
.1.3.6.1.4.1.34550.10.1.1.8.0 | InfraBoxMacAddress | Read Only | The MAC address of the InfraBox
.1.3.6.1.4.1.34550.10.1.1.9.0 | InfraBoxIpAddressIpv4 | Read Only | The IPv4 address of the InfraBox
.1.3.6.1.4.1.34550.10.1.1.10 | InfraBoxSubnetIpv4 | Read Only | The IPv4 subnet of the InfraBox
.1.3.6.1.4.1.34550.10.1.1.11.0 | InfraBoxGatewayIpv4 | Read Only | The IPv4 gateway of the InfraBox
.1.3.6.1.4.1.34550.10.1.1.12.0 | InfraBoxSolutionType | Read Only | 1 = InfraSolution , 2 = InfraGuard , 3 = InfraPower
.1.3.6.1.4.1.34550.10.1.1.13.0 | InfraBoxSolutionFirmwareInformation | Read Only | The firmware version of the InfraBox
.1.3.6.1.4.1.34550.10.2 | handleGroup | N/A | N/A
.1.3.6.1.4.1.34550.10.2.1 | handleAdmin | N/A | N/A
.1.3.6.1.4.1.34550.10.2.1.1 | handleTable | N/A | Table of handle entries
.1.3.6.1.4.1.34550.10.2.1.1.1 | handleEntry | N/A | Entries of handle
.1.3.6.1.4.1.34550.10.2.1.1.1.1.[1..2] | handleIndex | Read Only | The index of this handle , Level : 1 to 2 .1.3.6.1.4.1.34550.10.2.1.1.1.1.1 = front handle .1.3.6.1.4.1.34550.10.2.1.1.1.1.2 = rear handle
.1.3.6.1.4.1.34550.10.2.1.1.1.2.[1..2] | handleModel | Read Only | handle model , Length : 1 to 32 char. The model is fixed to " xHandle_model " .1.3.6.1.4.1.34550.10.2.1.1.1.2.1 = front handle .1.3.6.1.4.1.34550.10.2.1.1.1.2.2 = rear handle
.1.3.6.1.4.1.34550.10.2.1.1.1.4.[1..2] | handleName | Read Only | The name of handle , Length : 1 to 32 char. The name is fixed to " xHandle_name " .1.3.6.1.4.1.34550.10.2.1.1.1.4.1 = front handle .1.3.6.1.4.1.34550.10.2.1.1.1.4.2 = rear handle
.1.3.6.1.4.1.34550.10.2.1.1.1.5.[1..2] | handleBelongToRack | Read Only | The rack which the handle is installed , Length : 1 to 32 char. The name is fixed to " Demo_Rack_A " .1.3.6.1.4.1.34550.10.2.1.1.1.5.1 = front handle .1.3.6.1.4.1.34550.10.2.1.1.1.5.2 = rear handle
.1.3.6.1.4.1.34550.10.2.1.1.1.6.[1..2] | handleBelongToZone | Read Only | The zone where the handle is installed , Length : 1 to 32 char. The name is fixed to " Demo_Zone_A " .1.3.6.1.4.1.34550.10.2.1.1.1.6.1 = front handle .1.3.6.1.4.1.34550.10.2.1.1.1.6.2 = rear handle
.1.3.6.1.4.1.34550.10.2.1.1.1.7.[1..2] | handleLocation | Read Only | Which door the handle is installed , Length : 1 to 32 char. Value = front / rear .1.3.6.1.4.1.34550.10.2.1.1.1.7.1 = front door .1.3.6.1.4.1.34550.10.2.1.1.1.7.2 = rear door
.1.3.6.1.4.1.34550.10.2.1.1.1.8.[1..2] | handleReaderType | Read Only | The reader type of the handle , Length : 1 to 32 char. Value = Proximity / Mifare / iClass .1.3.6.1.4.1.34550.10.2.1.1.1.8.1 = front handle .1.3.6.1.4.1.34550.10.2.1.1.1.8.2 = rear handle
.1.3.6.1.4.1.34550.10.2.1.1.1.11.[1..2] | handleConnectionStatus | Read Only | The connection status of the handle , Length : 1 to 32 char. Status = Connected / Disconnected .1.3.6.1.4.1.34550.10.2.1.1.1.11.1 = front handle .1.3.6.1.4.1.34550.10.2.1.1.1.11.2 = rear handle
.1.3.6.1.4.1.34550.10.2.1.1.1.12.[1..2] | handleLastAccessCardNo | Read Only | The previous card no. which unlock the handle , Length = 8 decimal digital number. Range : 00000001 to 99999999. If the return value is 00000000, it means remote open / key open / unauthorized open
.1.3.6.1.4.1.34550.10.2.1.1.1.13.[1..2] | handleLastOpenTime | Read Only | The previous time stamp of the handle being opened Format : yymmddhhnnss ( 150702134520 = 02-Jul-2015 13:45:20 )
.1.3.6.1.4.1.34550.10.2.1.1.1.14.[1..2] | handleLastCloseTime | Read Only | The previous time stamp of the handle being closed Format : yymmddhhnnss ( 150702144520 = 02-Jul-2015 14:45:20 )
.1.3.6.1.4.1.34550.10.2.1.1.1.15.[1..2] | handleLastAccessDuration | Read Only | The last door open duration Format : ddhhnnss ( e.g. 1d 3h 37m 15s = 27hrs 37mins 15secs )
.1.3.6.1.4.1.34550.10.2.1.1.1.17.[1..2] | handleAlarmState | Read Only | The handle status. Length : 1 char. 0 = normal , 1 = alarm
.1.3.6.1.4.1.34550.10.2.1.1.1.18.[1..2] | handleAccessMode | Read Only | Access mode of handle which indicates the handle lock position. Length = 1 char 0 = key mode ( lock in 9 o'clock position ) , 1 = card mode ( lock in 12 o'clock position )
.1.3.6.1.4.1.34550.10.2.1.1.1.19.[1..2] | handleDoorSensorState | Read Only | The status of door sensor , Length = 1 char. 0 = door close , 1 = door open ( It does not mean the handle is locked or unlocked , please refer to the below OID value for the handle status )
.1.3.6.1.4.1.34550.10.2.1.1.1.20.[1..2] | handleLockState | Read Only | The handle lock status , Length =1. 0 = locked , 1 = unlocked
.1.3.6.1.4.1.34550.10.2.1.5 | handleControl | N/A | N/A
.1.3.6.1.4.1.34550.10.2.1.5.1 | FrontHandleControl | N/A | N/A
.1.3.6.1.4.1.34550.10.2.1.5.1.5 | SetFrontHandleRemoteRelease | Read / Write | Get the handle lock status , Length = 1 char. 0 = locked , 1 = unlocked. Set to remote unlock the handle lock, Length = 1 char. 1 = confirm the remote unlock the handle
.1.3.6.1.4.1.34550.10.2.1.5.2 | RearHandleControl | N/A | N/A
.1.3.6.1.4.1.34550.10.2.1.5.2.5 | SetRearHandleRemoteRelease | Read / Write | Get the handle lock status , Length = 1 char. 0 = locked , 1 = unlocked. Set to remote unlock the handle lock, Length = 1 char. 1 = confirm the remote unlock the handle
.1.3.6.1.4.1.34550.10.2.2 | handleTraps | N/A | N/A
.1.3.6.1.4.1.34550.10.2.2.1 | handleUnlockRemotely | N/A | When handle is unlocked remotely, this trap will send out once.
.1.3.6.1.4.1.34550.10.2.2.2 | handleLocked | N/A | When handle is locked, this trap will send out once.
.1.3.6.1.4.1.34550.10.2.2.3 | doorNormalOpen | N/A | When door is opened normally, this trap will send out once.
.1.3.6.1.4.1.34550.10.2.2.4 | doorClose | N/A | When door is closed, this trap will send out once.
.1.3.6.1.4.1.34550.10.2.2.6 | handleKeyAccess | N/A | When the handle is unlocked by key, this trap will send out once.
.1.3.6.1.4.1.34550.10.2.2.7 | handleAuthorizedCardAccess | N/A | When handle is unlocked by an authorized card, this trap will send out once.
.1.3.6.1.4.1.34550.10.2.2.8 | handleUnauthorizedCard | N/A | When an unauthorized card is present to the handle, this trap will send out once.
.1.3.6.1.4.1.34550.10.2.2.9 | doorAlarmOpem | N/A | When the door is opened unauthorizedly, this trap will send out once.
.1.3.6.1.4.1.34550.10.2.2.12 | doorAlarmStop | N/A | When unauthorized door open alarm is stopped, this trap will send out once.
.1.3.6.1.4.1.34550.10.3 | pduGroup | N/A | N/A
.1.3.6.1.4.1.34550.10.3.1 | pduAdmin | N/A | N/A
.1.3.6.1.4.1.34550.10.3.1.1 | pduTable | N/A | Table of PDU
.1.3.6.1.4.1.34550.10.3.1.1.1 | pduEntry | N/A | Table Entries of PDU
.1.3.6.1.4.1.34550.10.3.1.1.1.1.[1..4] | pduIndex | Read Only | PDU level in the InfraBox , Level : 1 to 4 .1.3.6.1.4.1.34550.10.3.1.1.1.1.1 = PDU level 1 .1.3.6.1.4.1.34550.10.3.1.1.1.1.14 = PDU level 4
.1.3.6.1.4.1.34550.10.3.1.1.1.2.[1..4] | pduModel | Read Only | PDU model No. , Level : 1 to 4 .1.3.6.1.4.1.34550..10.3.1.1.1.2.1 = PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.2.4 = PDU level 4
.1.3.6.1.4.1.34550.10.3.1.1.1.3.[1..4] | pduID | Read Only | PDU unique identifier , Level : 1 to 4 .1.3.6.1.4.1.34550..10.3.1.1.1.3.1 = PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.3.4 = PDU level 4
.1.3.6.1.4.1.34550.10.3.1.1.1.6.[1..4] | pduName | Read Only | The name of PDU , Level : 1 to 4 Length : 1 to 16 char. Space, single quote, double quote, #, %, &, ; and \ are reserved. They will be replaced by " _ "
.1.3.6.1.4.1.34550..10.3.1.1.1.7.[1..4] | pduLocation | Read Only | The Location of PDU , Level : 1 to 4 Length : 1 to 16 char. Space, single quote, double quote, #, %, &, ; and \ are reserved. They will be replaced by " _ "
.1.3.6.1.4.1.34550..10.3.1.1.1.8.[1..4] | pduGroupNumber | Read Only | The number indicates the IP dongle group the PDU belongs to when using InfraPower Management Software. Group number : from 000 to 240
.1.3.6.1.4.1.34550..10.3.1.1.1.13.[1..4] | pduMainLoadVoltage | Read Only | The measured input voltage of the PDU, Level : 1 to 4 .1.3.6.1.4.1.34550..10.3.1.1.1.13.1 = PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.13.4 = PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.14.[1..4] | pduMainLoadAmp | Read Only | The current load ampere of the PDU measured in tenth of amp. Level : 1 to 4 0 = 0.0A , 1 = 0.1A , 135 = 13.5A .1.3.6.1.4.1.34550..10.3.1.1.1.14.1 = PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.14.4 = PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.16.[1..4] | pduMainPowerFactor | Read Only | The power factor of the PDU measured in hundredth. Level : 1 to 4 000 = 0 , 001 = 0.01 , 055 = 0.55 , 100 = 1.0 .1.3.6.1.4.1.34550..10.3.1.1.1.16.1 = PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.16.4 = PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.17.[1..4] | pduMainActivePower | Read Only | The power consumption of the PDU measured in hundredth of W Range : 0000000 to 9999999 0 = 0W , 25 = 0.25W , 123 = 1.23W , 1234567 = 12345.67W
.1.3.6.1.4.1.34550..10.3.1.1.1.18.[1..4] | pduMainApparentPower | Read Only | The power consumption of the PDU measured in hundredth of VA Range : 0000000 to 9999999 0 = 0VA , 25 = 0.25VA, 123 = 1.23VA , 1234567 = 12345.67VA
.1.3.6.1.4.1.34550..10.3.1.1.1.19.[1..4] | pduMainCumulativeEnergy | Read Only | The accumulated energy consumption of the PDU in hundredth of kWh Range : 00000000 to 99999999 0 = 0.00kWh , 123 = 1.23kWh , 12345 = 123.45kWh , 12345678 = 123456.78kWh
.1.3.6.1.4.1.34550..10.3.1.1.1.20.[1..4] | pduRealClock | Read Only | The real time of the PDU. Format : YYMMDDHHNNSSW 1503281759596 = 2015-Mar-28 17:59:59 Saturday
.1.3.6.1.4.1.34550..10.3.1.1.1.24 | circuits | N/A | N/A
.1.3.6.1.4.1.34550..10.3.1.1.1.24.1 | circuitTable | N/A | Table of Circuit
.1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1 | circuitTableEntry | N/A | Table of Circuit Entries
.1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.1.[1..4].[1..2] | circuitIndex | Read Only | The ID of the PDU's circuit , 1 = Circuit A , 2 = Circuit B .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.1.1.1 = Circuit A of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.1.4.2 = Circuit B of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.2.[1..4].[1..2] | circuitRatedAmp | Read Only | The input current rating of the PDU's circuit in tenth of amp. Value : 100 = 10.0A , 160 = 16.0A , 200 = 20.0A .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.2.1.1 = Circuit A of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.2.4.2 = Circuit B of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.5.[1..4].[1..2] | circuitState | Read Only | The status of the PDU's circuit. Value : 0 = Normal, 1 = Alarm , 2 = Rising alert , 3 = Low alert , 4 = circuit not exist .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.5.1.1 = Circuit A of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.5.4.2 = Circuit B of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.6.[1..4].[1..2] | circuitLoadVoltage | Read Only | The voltage of the PDU's circuit measured in tenth of volt. Value : 0000 = 0.0VAC , 1100 = 110.0VAC , 2225 = 222.5VAC .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.6.1.1 = Circuit A of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.6.4.2 = Circuit B of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.7.[1..4].[1..2] | circuitLoadAmp | Read Only | The current load ampere of the PDU's circuit measured in tenth of amp. Value : 000 = 0.0A , 001 = 0.01A , 105 = 10.5A .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.7.1.1 = Circuit A of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.7.4.2 = Circuit B of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.12.[1..4].[1..2] | circuitLoadPeakAmp | Read Only | The peak load ampere of the PDU's circuit recorded in tenth of amp with timestamp. 150330105959@081 = 2015-Mar-30 10:59:59 , 8.1A .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.12.1.1 = Circuit A of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.12.4.2 = Circuit B of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.13.[1..4].[1..2] | circuitCumulativeEnergy | Read Only | The accumulated energy consumption of the PDU's circuit in hundredth of kWh with timestamp Range : 00000000 to 99999999 150330105959@09999999 = 2015-Mar-30 10:59:59 , 99999.99kWh .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.14.1.1 = Circuit A of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.14.4.2 = Circuit B of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.15.[1..4].[1..2] | circuitBreakerStateCopy | Read Only | The circuit breaker state of the PDU. 0 = normal , 1 = tripped .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.15.1.1 = Circuit A of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.15.4.2 = Circuit B of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.16.[1..4].[1..2] | circuitLoadAmpAlarmThresh | Read Only | The current load ampere alarm threshold of the PDU's circuit in tenth of amp. 001 = 0.1A , 050 = 5.0A , 130 = 13.0A .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.16.1.1 = Circuit A of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.16.4.2 = Circuit B of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.16.[1..4].[1..2] | circuitLoadAmpAlarmThresh | Read Only | The current load ampere rising alert threshold of the PDU's circuit in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.17.1.1 = Circuit A of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.17.4.2 = Circuit B of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.18.[1..4].[1..2] | circuitLoadAmpLowAlertThresh | Read Only | The current load ampere low alert threshold of the PDU's circuit in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.18.1.1 = Circuit A of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.24.1.1.18.4.2 = Circuit B of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.25 | circuitBreakers | N/A | N/A
.1.3.6.1.4.1.34550..10.3.1.1.1.25.1 | circuitBreakerTable | N/A | Table of circuit breaker
.1.3.6.1.4.1.34550..10.3.1.1.1.25.1.1 | circuitBreakerTableEntry | N/A | Table entries of circuit breaker
.1.3.6.1.4.1.34550..10.3.1.1.1.25.1.1.1.[1..4].[1..2] | circuitBreakerIndex | Read Only | The ID of the PDU's circuit breaker. 1 = circuit A's circuit breaker, 2 = circuit B's circuit breaker .1.3.6.1.4.1.34550..10.3.1.1.1.25.1.1.1.1.1 = circuit A of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.25.1.1.1.4.2 = circuit B of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.25.1.1.2.[1..4].[1..2] | circuitBreakerRatedAmp | Read Only | The current rating of the PDU's circuit breaker in tenth of amp. 100 = 10.0A , 160 = 16.0A , 200 = 20.0A .1.3.6.1.4.1.34550..10.3.1.1.1.25.1.1.2.1.1 = Circuit A's circuit breaker of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.25.1.1.2.4.2 = Circuit B's circuit breaker of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.25.1.1.4.[1..4].[1..2] | circuitBreakerState | Read Only | The circuit breaker state of the PDU. 0 = normal , 1 = tripped .1.3.6.1.4.1.34550..10.3.1.1.1.25.1.1.4.1.1 = Circuit A's circuit breaker of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.25.1.1.4.4.2 = Circuit B's circuit breaker of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26 | outlets | N/A
.1.3.6.1.4.1.34550..10.3.1.1.1.26.1 | stdOutletTable | N/A | Table of non - C19 outlet
.1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1 | stdOutletTableEntry | N/A | Table entries of non - C19 outlet
.1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.1.[1..4].[1..48] | stdOutletIndex | Read Only | The ID of the PDU's non - C19 outlet. Range : 1 to 48. 1 = outlet 01, 48 = outlet 48 .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.1.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.1.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.2.[1..4].[1..48] | stdOutletCircuit | Read Only | The circuit of the outlet belongs to. 1 = circuit A , 2 = circuit B .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.2.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.2.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.3.[1..4].[1..48] | stdOutletType | Read Only | The type of non - C19 outlet. 1 = IEC C13 , 2 = NEMA 5-20 , 3 = BS1363 , 4 = Schuko , 5 = French , 6 = AS 3112 .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.3.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.3.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.4.[1..4].[1..48] | stdOutletName | Read Only | The name of the outlet. Range : 1 to 16 char. .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.4.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.4.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.7.[1..4].[1..48] | stdOutletPowerStatus | Read Only | The power state of the outlet. 0 = OFF , 1 = ON .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.7.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.7.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.8.[1..4].[1..48] | stdOutletAlarmState | Read Only | The alarm state of the outlet. 0 = Normal, 1 = Alarm , 2 = Rising alert , 3 = Low alert .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.8.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.8.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.9.[1..4].[1..48] | stdOutletLoadAmp | Read Only | The current load ampere of the outlet measured in tenth of amp. 000 = 0.0A , 001 = 0.01A , 105 = 10.5A , " --- " = immeasurable .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.9.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.9.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.10.[1..4].[1..48] | stdOutletEnergy | Read Only | The power consumption of the PDU's outlet measured in hundredth of Watt. Range : 0000000 to 9999999 0 = 0W , 25 = 0.25W , 123 = 1.23W , 1234567 = 12345.67W .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.10.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.10.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.11.[1..4].[1..48] | stdOutletPeakAmp | Read Only | The peak load ampere of the outlet recorded in tenth of amp with timestamp. 150330105959@031 = 2015-Mar-30 10:59:59 , 3.1A .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.11.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.11.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.12.[1..4].[1..48] | stdOutletCumulativeEnergy | Read Only | The accumulated energy consumption of the outlet in hundredth of kWh with timestamp Range : 00000000 to 99999999 150330105959@09999999 = 2015-Mar-30 10:59:59 , 99999.99kWh .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.12.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.2.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.13.[1..4].[1..48] | stdOutletLoadAmpAlarmThresh | Read Only | The current load ampere alarm threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.13.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.13.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.14.[1..4].[1..48] | stdOutletLoadAmpRisingAlertThresh | Read Only | The current load ampere rising alert threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.14.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.14.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.15.[1..4].[1..48] | stdOutletLoadAmpLowAlertThresh | Read Only | The current load ampere low alert threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.15.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.15.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.18.[1..4].[1..48] | stdOutletPowerUpSequenceDelay | Read Only | The sequential power up interval between outlet in second. Range : 1 to 10 sec. Set : 0 = 1 sec , 5 = 6 sec , 9 = 10 sec .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.18.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.1.1.18.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.2 | c19OutletTable | N/A | Table of C19 outlet
.1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1 | c19OutletTableEntry | N/A | Table entries of C19 outlet
.1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.1.[1..4].[1..48] | c19OutletIndex | Read Only | The ID of the PDU's C19 outlet. Range : 1 to 48. 1 = outlet 01, 48 = outlet 48 .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.1.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.1.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.2.[1..4].[1..48] | c19OutletCircuit | Read Only | The circuit of the outlet belongs to. 1 = circuit A , 2 = circuit B .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.2.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.2.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.3.[1..4].[1..48] | c19OutletType | Read Only | The type of C19 outlet. 1 = IEC C13 , 2 = IEC C19 , 3 = BS1363 , 4 = NEMA 5-20 , 5 = CEE7 .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.3.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.3.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.4.[1..4].[1..48] | c19OutletName | Read Only | The name of the outlet. Range : 1 to 16 char. .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.4.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.4.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.7.[1..4].[1..48] | c19OutletPowerStatus | Read Only | The power state of the outlet. 0 = OFF , 1 = ON .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.7.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.7.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.8.[1..4].[1..48] | c19OutletAlarmState | Read Only | The alarm state of the outlet. 0 = Normal, 1 = Alarm , 2 = Rising alert , 3 = Low alert .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.8.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.8.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.9.[1..4].[1..48] | c19OutletLoadAmp | Read Only | The current load ampere of the outlet measured in tenth of amp. 000 = 0.0A , 001 = 0.01A , 105 = 10.5A , " --- " = immeasurable .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.9.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.9.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.10.[1..4].[1..48] | c19OutletEnergy | Read Only | The power consumption of the PDU's outlet measured in hundredth of Watt. Range : 0000000 to 9999999 0 = 0W , 25 = 0.25W , 123 = 1.23W , 1234567 = 12345.67W .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.10.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.10.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.11.[1..4].[1..48] | c19OutletPeakAmp | Read Only | The peak load ampere of the outlet recorded in tenth of amp with timestamp. 150330105959@031 = 2015-Mar-30 10:59:59 , 3.1A .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.11.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.11.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.12.[1..4].[1..48] | c19OutletCumulativeEnergy | Read Only | The accumulated energy consumption of the outlet in hundredth of kWh with timestamp Range : 00000000 to 99999999 150330105959@09999999 = 2015-Mar-30 10:59:59 , 99999.99kWh .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.12.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.2.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.13.[1..4].[1..48] | c19OutletLoadAmpAlarmThresh | Read Only | The current load ampere alarm threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.13.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.13.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.14.[1..4].[1..48] | c19OutletLoadAmpRisingAlertThresh | Read Only | The current load ampere rising alert threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.14.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.14.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.15.[1..4].[1..48] | c19OutletLoadAmpLowAlertThresh | Read Only | The current load ampere low alert threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.15.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.15.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.18.[1..4].[1..48] | c19OutletPowerUpSequenceDelay | Read Only | The sequential power up interval between outlet in second. Range : 1 to 10 sec. Set : 0 = 1 sec , 5 = 6 sec , 9 = 10 sec .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.18.1.1 = Outlet 01 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.26.2.1.18.4.48 = Outlet 48 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.27 | THSensors | N/A | N/A
.1.3.6.1.4.1.34550..10.3.1.1.1.27.1 | THSensorsTable | N/A | Table of TH sensors
.1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1 | THSensorsTableEntry | N/A | Table entries of TH sensors
.1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.1.[1..4].[1..2] | THSensorIndex | Read Only | The ID of TH sensors. 1 = TH 1 , 2 = TH 2 .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.1.1.1 = TH1 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.1.4.2 = TH2 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.3.[1..4].[1..2] | THSensorLocation | Read Only | The location of TH sensor. Range : 1 to 16 char. .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.3.1.1 = TH1 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.3.4.2 = TH2 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.4.[1..4].[1..2] | THSensorType | Read Only | The type of the sensor. 1 = Temp. sensor , 2 = Temp + Humid sensor .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.4.1.1 = TH1 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.4.4.2 = TH2 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.5.[1..4].[1..2] | THSensorConnState | Read Only | The connection status of the sensor. 0 = disconnected , 1 = connected .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.5.1.1 = TH1 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.5.4.2 = TH2 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.6.[1..4].[1..2] | THSensorAlarmState | Read Only | The alarm state of the sensor. 0 = normal , 1 = humid sensor alarm only , 10 = temp. sensor alarm only , 11 = temp + humid sensor alarm .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.6.1.1 = TH1 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.6.4.2 = TH2 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.7.[1..4].[1..2] | tempSensorValue | Read Only | The temp. measured in tenth of Degree Celsius 0 = 0C , 10 = 1C , 123 = 12.3C , 999 = 99.9C .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.7.1.1 = TH1 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.7.4.2 = TH2 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.8.[1..4].[1..2] | tempSensorValueStr | Read Only | The temp. measured in tenth of Degree Celsius ---- = disconnected , 0000 = 0C , 0010 = 1C , 0123 = 12.3C , 0999 = 99.9C .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.8.1.1 = TH1 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.8.4.2 = TH2 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.9.[1..4].[1..2] | tempSensorUpperAlarmThresh | Read Only | The temp. alarm threshold in tenth of Degree Celsius 0000 = 0C , 0010 = 1C , 0123 = 12.3C , 0999 =99.9C .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.9.1.1 = TH1 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.9.4.2 = TH2 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.10.[1..4].[1..2] | tempSensorRisingAlertThresh | Read Only | The temp. rising alert threshold in tenth of Degree Celsius 0000 = disable , 0010 = 1C , 0123 = 12.3C , 0999 =99.9C .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.10.1.1 = TH1 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.10.4.2 = TH2 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.11.[1..4].[1..2] | humiSensorValue | Read Only | The relative humidity measured in tenth of percentage. 0 = 0% , 1 = 0.1% , 255 = 25.5% , 999 = 99.9% .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.11.1.1 = TH1 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.11.4.2 = TH2 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.12.[1..4].[1..2] | humiSensorValueStr | Read Only | The relative humidity measured in tenth of percentage. ---- = disconnected , 000 = 0% , 001 = 0.1% , 025 = 2.5% , 999 = 99.9% .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.12.1.1 = TH1 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.12.4.2 = TH2 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.13.[1..4].[1..2] | humiSensorUpperAlarmThresh | Read Only | The relative humidity alarm threshold in tenth of percentage 000 = 0% , 001 = 0.1% , 025 = 2.5% , 999 = 99.9% .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.13.1.1 = TH1 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.13.4.2 = TH2 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.14.[1..4].[1..2] | humiSensorRisingAlertThresh | Read Only | The relative humidity rising alert threshold in tenth of percentage 000 = disable , 001 = 0.1% , 025 = 2.5% , 999 = 99.9% .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.14.1.1 = TH1 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.14.4.2 = TH2 of PDU level 4
.1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.15.[1..4].[1..2] | THSensorActivation | Read Only | The activation state of the Temp. or Temp. & humid. Sensor. 0 = deactivated , 1 = activated .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.15.1.1 = TH1 of PDU level 1 .1.3.6.1.4.1.34550..10.3.1.1.1.27.1.1.15.4.2 = TH2 of PDU level 4
.1.3.6.1.4.1.34550.10.3.1.5 | pduControl | N/A | N/A
.1.3.6.1.4.1.34550.10.3.1.5.1.0 | setPduName | Write Only | Set the PDU name. Length : 4 to 16 char. Space, single quote, double quote, #, %, &, ; and \ are reserved. They will be replaced by " _ " Value syntax : [ PDU_level ] [ pdu_name_text ] PDU_level : 1 to 4 , pdu_name_text : 4 to 16 char. e.g. P1.Cab001 = Set the name of PDU level 1 to Cab001
.1.3.6.1.4.1.34550.10.3.1.5.2.0 | SetPduLocation | Write Only | Set the PDU location. Length : 4 to 16 char. Space, single quote, double quote, #, %, &, ; and \ are reserved. They will be replaced by " _ " Value syntax : [ PDU_level ] [ pdu_location_text ] PDU_level : 1 to 4 , pdu_location_text : 4 to 16 char. e.g. P1.Rear_left = Set the location of PDU level 1 to Rear_left
.1.3.6.1.4.1.34550.10.3.1.5.10.0 | SetCircuitLoadPeakAmpReset | Write Only | Reset the PDU's circuit peak amp. to zero. 1 = confirm e.g. P1.CA.1 = reset the circuit A peak amp. of PDU level 1 to zero P4.CB.1 = reset the circuit B peak amp. of PDU level 4 to zero
.1.3.6.1.4.1.34550.10.3.1.5.11.0 | SetCircuitCumulativeEnergyReset | Write Only | Reset the PDU's circuit cumulative energy to zero. 1 = confirm e.g. P1.CA.1 = reset the circuit A cumulative energy of PDU level 1 to zero P4.CB.1 = reset the circuit B cumulative energy of PDU level 1 to zero
.1.3.6.1.4.1.34550.10.3.1.5.12.0 | SetCircuitLoadAmpAlarmThresh | Write Only | Set the PDU's circuit current alarm threshold in tenth of ampere. 010 = 1A , 100 = 10A Value syntax : [ PDU_level ] [ circuit_current_alarm_threshold ] e.g. P1.CA.130 = Set the circuit A current alarm threshold of PDU level 1 to 13A P4.CB.125 = reset the circuit B current alarm threshold of PDU level 4 to 12.5A
.1.3.6.1.4.1.34550.10.3.1.5.13.0 | SetCircuitLoadAmpRisingAlertThresh | Write Only | Set the PDU's circuit current rising alert threshold in tenth of ampere. 000 = disable , 010 = 1A , 100 = 10A Value syntax : [ PDU_level ] [ circuit_current_alarm_threshold ] Remarks : The rising alert threshold MUST BE lower than the alarm threshold e.g. P1.CA.130 = Set the circuit A current rising alert threshold of PDU level 1 to 13A P4.CB.125 = reset the circuit B current rising alert threshold of PDU level 4 to 12.5A
.1.3.6.1.4.1.34550.10.3.1.5.14.0 | SetCircuitLoadAmpLowAlertThresh | Write Only | Set the PDU's circuit current low alert threshold in tenth of ampere. 000 = disable , 010 = 1A , 100 = 10A Value syntax : [ PDU_level ] [ circuit_current_alarm_threshold ] Remarks : The low alert threshold MUST BE lower than the rising alert threshold e.g. P1.CA.130 = Set the circuit A current rising alert threshold of PDU level 1 to 13A P4.CB.125 = reset the circuit B current rising alert threshold of PDU level 4 to 12.5A
.1.3.6.1.4.1.34550.10.3.1.5.20.0 | SetOutletPowerOFF | Write Only | To switch OFF of the outlet power of the PDU. 0 = confirm Value syntax : [ PDU_level ] [ outlet_id ] e.g. P1.01.0 = Switch OFF the outlet 01 ( non-C19 outlet ) of PDU level 1 P4.C2.0 = Switch OFF the outlet C2 ( C-19 outlet ) of PDU level 4
.1.3.6.1.4.1.34550.10.3.1.5.21.0 | SetOutletPowerON | Write Only | To switch ON of the outlet power of the PDU. 1 = confirm Value syntax : [ PDU_level ] [ outlet_id ] e.g. P1.01.1 = Switch ON the outlet 01 ( non-C19 outlet ) of PDU level 1 P4.C2.1 = Switch ON the outlet C2 ( C-19 outlet ) of PDU level 4
.1.3.6.1.4.1.34550.10.3.1.5.22.0 | SetOultletName | Write Only | Set the outlet name. Length : 4 to 16 char. Space, single quote, double quote, #, %, &, ; and \ are reserved. They will be replaced by " _ " Value syntax : [ PDU_level ] [ outlet_id ] [ outlet_name ] e.g. P1.01.Server001 : Set the name of PDU level 1's outlet 01 to Server001 P4.C4.Server016 : Set the name of PDU level 4's outlet C4 to Server016
.1.3.6.1.4.1.34550.10.3.1.5.23.0 | SetOutletDelaySwitchONCount | Write Only | Set the outlet power on delay time. Range : 0 ~ 9 ( 1 to 10 seconds ) Value syntax : [ PDU_level ] [ Outlet_id ] [ delay_on_time ] e.g. P1.01.1 : Set the delay on time of outlet 01 of PDU level 1 to 2 second P4.C4.9 : Set the delay on time of outet C4 of PDU level 4 to 10 seconds
.1.3.6.1.4.1.34550.10.3.1.5.24.0 | SetOutletLoadPeakAmpReset | Write Only | Reset the PDU's outlet peak amp. to zero. 1 = confirm Value syntax : [ PDU_level ] [ outlet_id ] e.g. P1.01.1 = reset the outlet 01 ( non C-19 outlet ) peak amp. of PDU level 1 to zero P4.C10.1 = reset the outlet C10 ( C-19 outlet ) peak amp. of PDU level 4 to zero
.1.3.6.1.4.1.34550.10.3.1.5.25.0 | SetOutletCumulativeEnergyReset | Write Only | Reset the PDU's outlet cumulative energy to zero. 1 = confirm Value syntax : [ PDU_level ] [ outlet_id ] e.g. P1.01.1 = reset the outlet 01 ( non C-19 outlet ) cumulative energy. of PDU level 1 to zero P4.C10.1 = reset the outlet C10 ( C-19 outlet ) cumulative energy. of PDU level 4 to zero
.1.3.6.1.4.1.34550.10.3.1.5.26.0 | SetOutletLoadAmpAlarmThresh | Write Only | Set the PDU's outlet current alarm threshold in tenth of ampere. 010 = 1A , 100 = 10A Value syntax : [ PDU_level ] [ outlet_current_alarm_threshold ] e.g. P1.01.130 = Set the outlet 01 ( non C-19 outlet ) current alarm threshold of PDU level 1 to 13A P4.C10.125 = Set the outlet C10 ( C-19 outlet ) current alarm threshold of PDU level 4 to 12.5A
.1.3.6.1.4.1.34550.10.3.1.5.27.0 | SetOutletLoadAmpRisingAlertThresh | Write Only | Set the PDU's outlet current rising alert threshold in tenth of ampere. 010 = 1A , 100 = 10A Value syntax : [ PDU_level ] [ outlet_current_rising_alert_threshold ] Remarks : The rising alert threshold MUST BE lower than the alarm threshold e.g. P1.01.130 = Set the outlet 01 ( non C-19 outlet ) current rising alert threshold of PDU level 1 to 13A P4.C10.125 = Set the outlet C10 ( C-19 outlet ) current rising alert threshold of PDU level 4 to 12.5A
.1.3.6.1.4.1.34550.10.3.1.5.28.0 | SetOutletLoadAmpLowAlertThresh | Write Only | Set the PDU's outlet current low alert threshold in tenth of ampere. 010 = 1A , 100 = 10A Value syntax : [ PDU_level ] [ outlet_current_low_alert_threshold ] Remarks : The low alert threshold MUST BE lower than the rising alert threshold e.g. P1.01.130 = Set the outlet 01 ( non C-19 outlet ) current low alert threshold of PDU level 1 to 13A P4.C10.125 = Set the outlet C10 ( C-19 outlet ) current low alert threshold of PDU level 4 to 12.5A
.1.3.6.1.4.1.34550.10.3.1.5.30.0 | SetTHSensorActivate | Write Only | Activate the TH sensor of the PDU. 1 = confirm Value Syntax : [ PDU_level ] [ TH_sensor_id ] e.g. P1.T1.1 = Activate the TH sensor 1 of PDU level 1 P4.T2.1 = Activate the TH sensor 2 of PDU level 4
.1.3.6.1.4.1.34550.10.3.1.5.31.0 | SetTHSensorDeactivate | Write Only | Deactivate the TH sensor of the PDU. 0 = confirm Value Syntax : [ PDU_level ] [ TH_sensor_id ] e.g. P1.T1.1 = Deactivate the TH sensor 1 of PDU level 1 P4.T2.1 = Deactivate the TH sensor 2 of PDU level 4
.1.3.6.1.4.1.34550.10.3.1.5.32.0 | SetTHSensorLocation | Write Only | Set the PDU's TH sensor location. Length : 4 to 16 char. Space, single quote, double quote, #, %, &, ; and \ are reserved. They will be replaced by " _ " Value syntax : [ PDU_level ] [ TH_sensor_id ] [ TH_location_text ] e.g. P1.T1.Front_Door = Set the location of TH sensor 1 of PDU level 1 to Front_Door L16.P4.T2.Rear_Door = Set the location of TH sensor 2 of PDU level 4 to Rear_Door
.1.3.6.1.4.1.34550.10.3.1.5.33.0 | SetTHSensorTempAlarmThreshold | Write Only | Set the PDU's Temp Sensor Alarm Threshold in tenth of degree Celsuis. Range : 0000 to 9999 Value syntax : [ PDU_level ] [ TH_sensor_id ] [ Temp_alarm ] e.g. P1.T1.0300 = Set the Alarm Threshold of Temp. 1 of PDU level 1 to 30 degree Celsuis P4.T2.0400 = Set the Alarm Threshold of Temp. 2 of PDU level 4 to 40 degree Celsuis
.1.3.6.1.4.1.34550.10.3.1.5.34.0 | SetTHSensorTempRisingAlertThreshold | Write Only | Set the PDU's Temp Sensor Rising Alert Threshold in tenth of degree Celsuis. Range : 0000 to 9999. 0000 = disable Remarks : The Rising Alert Threshold MUST BE lower than the Alarm Threshold Value syntax : [ PDU_level ] [ TH_sensor_id ] [ Temp_rising_alert ] e.g. P1.T1.0250 = Set the Rising Alert Threshold of Temp. 1 of PDU level 1 to 25 degree Celsuis P4.T2.0300 = Set the Rising Alert Threshold of Temp. 2 of PDU level 4 to 30 degree Celsuis
.1.3.6.1.4.1.34550.10.3.1.5.35.0 | SetTHSensorHumidAlarmThreshold | Write Only | Set the PDU's Humid Sensor Alarm Threshold in tenth of percent. Range : 001 to 999 Value syntax : [ PDU_level ] [ TH_sensor_id ] [ Humid_alarm ] e.g. P1.T1.600 = Set the Alarm Threshold of Humid. 1 of PDU level 1 to 60% P4.T2.950 = Set the Alarm Threshold of Humid. 2 of PDU level 4 to 95%
.1.3.6.1.4.1.34550.10.3.1.5.36.0 | SetTHSensorHumidRisingAlertThreshold | Write Only | Set the PDU's Humid Sensor Rising Alert Threshold in tenth of percent. Range : 001 to 999. 000 = disable Remarks : The Rising Alert Threshold MUST BE lower than the Alarm Threshold Value syntax : [ PDU_level ] [ TH_sensor_id ] [ Humid_rising_alert ] e.g. P1.H1.500 = Set the Rising Alert Threshold of Humid. 1 of PDU level 1 to 50% P4.H2.900 = Set the Rising Alert Threshold of Humid. 2 of PDU level 4 to 90%
.1.3.6.1.4.1.34550..10.3.2 | pduTraps | N/A
.1.3.6.1.4.1.34550..10.3.2.1 | circuitLoadEventTriggered | N/A | A trap will send out in cycle when the circuit level current load over the circuit amp. alarm threshold. It will stop when the cirucit level current load is below the circuit amp. alarm threshold. The time interval for one cycle is within 1 min if 4 PDUs are connected.
.1.3.6.1.4.1.34550..10.3.2.2 | c19OutletLoadEventTriggered | N/A | A trap will send out in cycle when outlet current load over the outlet amp. alarm threshold. It will stop when the outlet current load is below the outlet amp. alarm threshold. The time interval for one cycle is within 1 min if 4 PDUs are connected.
.1.3.6.1.4.1.34550..10.3.2.3 | stdOutletLoadEventTriggered | N/A | A trap will send out in cycle when outlet current load over the outlet amp. alarm threshold. It will stop when the outlet current load is below the outlet amp. alarm threshold. The time interval for one cycle is within 1 min if 4 PDUs are connected.
.1.3.6.1.4.1.34550..10.3.2.12 | circuitBreakerTripped | N/A | A trap will send out in cycle when the circuit breaker is tripped. The time interval for one cycle is within 1 min if 4 PDUs are connected.
.1.3.6.1.4.1.34550..10.3.2.13 | circuitBreakerRecovered | N/A | A trap will send out when the circuit breaker is resumed normal.
.1.3.6.1.4.1.34550..10.3.2.40 | tempHumiSenosorConnLost | N/A | A trap will send out in cycle when the Temp. or Temp. & humid sensor is disconnected. It will stop when the Temp. or Temp. & humid sensor is reconnected. The time interval for one cycle is within 1 min if 4 PDUs are connected.
.1.3.6.1.4.1.34550..10.3.2.41 | tempSesnorUpperAlarmTriggered | N/A | A trap will send out in cycle when the temp. reading is over the temp. alarm threshold. It will stop when the temp. reading is below the temp. alarm threshold. The time interval for one cycle is within 1 min if 4 PDUs are connected.
.1.3.6.1.4.1.34550..10.3.2.47 | humiSensorUpperAlarmTriggered | N/A | A trap will send out in cycle when the relative humid. reading is over the humid. alarm threshold. It will stop when the relative humid. reading is below the humid. alarm threshold. The time interval for one cycle is within 1 min if 4 PDUs are connected.
.1.3.6.1.4.1.34550..10.3.2.53 | pduDisconnected | N/A | A trap will send out once when the PDU is disconnected.
.1.3.6.1.4.1.34550.30.5 | iBoxSensorGroup | N/A | N/A
.1.3.6.1.4.1.34550.30.5.1 | iBoxSensorAdmin | N/A | N/A
.1.3.6.1.4.1.34550.30.5.1.1 | iBoxSensorTable | N/A | Table of Sensor
.1.3.6.1.4.1.34550.30.5.1.1.1 | iBoxSensorEntry | N/A | Table entries of Sensor
.1.3.6.1.4.1.34550.30.5.1.1.1.1.[1..13] | iBoxSensorIndex | Read Only | The ID of the sensor of the InfraBox. Each InfraBox has 13 sensor ID. ( For X-2000 ONLY ) 1 = Temp 1 , 2 = Temp 2 , 3 = Humid 1 , 4 = Humid 2 , 5 = Smoke / Shock 1 , 6 = Smoke / Shock 2 7 = Water 1 , 8 = Water 2 , 9 = Lamp 1 , 10 = Lamp 2 , 11 = Beacon , 12 = Alarm out , 13 = Buzzer .1.3.6.1.4.1.34550.30.5.1.1.1.1.1 = Temp. 1 .1.3.6.1.4.1.34550.30.5.1.1.1.1.3 = Humid. 1 .1.3.6.1.4.1.34550.30.5.1.1.1.1.11 =Beacon .1.3.6.1.4.1.34550.30.5.1.1.1.1.13 = Buzzer
.1.3.6.1.4.1.34550.30.5.1.1.1.2.[1..13] | iBoxSensorModel | Read Only | The Model of the sensor of the InfraBox. Each InfraBox has 13 sensor ID. .1.3.6.1.4.1.34550.30.5.1.1.1.2.1 = Temp. 1 .1.3.6.1.4.1.34550.30.5.1.1.1.2.3 = Humid. 1 .1.3.6.1.4.1.34550.30.5.1.1.1.2.11 =Beacon .1.3.6.1.4.1.34550.30.5.1.1.1.2.13 = Buzzer
.1.3.6.1.4.1.34550.30.5.1.1.1.3.[1..13] | iBoxSensorName | Read Only | The Name of the sensor of the InfraBox. Each InfraBox has 13 sensor. Length : 4 to 16 char. .1.3.6.1.4.1.34550.30.5.1.1.1.3.1 = Temp. 1 .1.3.6.1.4.1.34550.30.5.1.1.1.3.3 = Humid. 1 .1.3.6.1.4.1.34550.30.5.1.1.1.3.11 =Beacon .1.3.6.1.4.1.34550.30.5.1.1.1.3.13 = Buzzer
.1.3.6.1.4.1.34550.30.5.1.1.1.4.[1..13] | iBoxSensorLocation | Read Only | The Location of the sensor of the InfraBox. Each InfraBox has 13 sensor. Length : 4 to 16 char. .1.3.6.1.4.1.34550.30.5.1.1.1.4.1 = Temp. 1 .1.3.6.1.4.1.34550.30.5.1.1.1.4.3 = Humid. 1 .1.3.6.1.4.1.34550.30.5.1.1.1.4.11 =Beacon .1.3.6.1.4.1.34550.30.5.1.1.1.4.13 = Buzzer
.1.3.6.1.4.1.34550.30.5.1.1.1.5.[1..13] | iBoxSensorType | Read Only | The Type of the sensor of the InfraBox. Each InfraBox has 13 sensor. T1 = Temp 1 , T2 = Temp 2 , H1 = Humid 1 , H2 = Humid 2 , S1 = Smoke / Shock 1 , S2 = Smoke / Shock 2 W1 = Water 1 , W2 = Water 2 , L1 = Lamp 1 , L2 = Lamp 2 , B1 = Beacon , A1 = Alarm out , Z1 = Buzzer , .1.3.6.1.4.1.34550.30.5.1.1.1.5.1 = Temp. 1 .1.3.6.1.4.1.34550.30.5.1.1.1.5.3 = Humid. 1 .1.3.6.1.4.1.34550.30.5.1.1.1.5.11 =Beacon .1.3.6.1.4.1.34550.30.5.1.1.1.5.13 = Buzzer
.1.3.6.1.4.1.34550.30.5.1.1.1.6.[1..13] | iBoxSensorAlarmThreshold | Read Only | The Alarm Threshold of the TH sensor of the InfraBox. The Temp Alarm Threshold in tenth of Degree Celsius, 0010 = 1 , 0300 = 30 , 0999 = 99.9 The Humid Alarm Threshold in tenth of percent, 001 = 1 , 050 = 50 , 099 = 99 .1.3.6.1.4.1.34550.30.5.1.1.1.6.1 = Temp 1 .1.3.6.1.4.1.34550.30.5.1.1.1.6.2 = Temp 2 .1.3.6.1.4.1.34550.30.5.1.1.1.6.3 = Humid 1 .1.3.6.1.4.1.34550.30.5.1.1.1.6.4 = Humid 2
.1.3.6.1.4.1.34550.30.5.1.1.1.9.[1..13] | iBoxSensorAlarmState | Read Only | The Alarm of the sensor of the InfraBox. Each EC Box has 13 sensor. 0 = Normal , 1 = Alarm , - = disconnected ( For lamp 1 & 2 , 0 = OFF , 1 = ON ) .1.3.6.1.4.1.34550.30.5.1.1.1.9.1 = Temp. 1 .1.3.6.1.4.1.34550.30.5.1.1.1.9.4 = Humid. 2 .1.3.6.1.4.1.34550.30.5.1.1.1.9.8 = Water 2 .1.3.6.1.4.1.34550.30.5.1.1.1.9.13 = Buzzer
.1.3.6.1.4.1.34550.30.5.1.1.1.10.[1..13] | iBoxSensorControlState | Read Only | The Control state of the TH sensor of the InfraBox which will be shown on the LED display of the InfraBox 0 = Off, 1 = On , 3 = Blink .1.3.6.1.4.1.34550.30.5.1.1.1.10.1 = Temp. 1 .1.3.6.1.4.1.34550.30.5.1.1.1.10.2 = Temp. 2 .1.3.6.1.4.1.34550.30.5.1.1.1.10.3 = Humid 1 .1.3.6.1.4.1.34550.30.5.1.1.1.10.4 = Humid 2
.1.3.6.1.4.1.34550.30.5.1.1.1.11.[1..13] | iBoxSensorReading | Read Only | The Reading of the TH sensor of the InfraBox. Temp. reading measured in tenth of degree Celsuis. --- = disconnected , 0000 = 0.0 , 0010 = 1 , 0999 =99.9 Humid reading measured in tenth of percent. --- = disconnected , 000 = 0 , 010 = 10 , 099 = 99 Remarks : All other sensors reading can be ignored .1.3.6.1.4.1.34550.30.5.1.1.1.11.1 = Temp. 1 .1.3.6.1.4.1.34550.30.5.1.1.1.11.2 = Temp. 2 .1.3.6.1.4.1.34550.30.5.1.1.1.11.3 = Humid 1 .1.3.6.1.4.1.34550.30.5.1.1.1.11.4 = Humid 2
.1.3.6.1.4.1.34550.30.5.1.1.1.13.[1..13] | iBoxSensorActivation | Read Only | The Activation state of the sensor of the InfraBox. Each EC Box has 13 sensor. 0 = Deactivated , 1 = Activated .1.3.6.1.4.1.34550.30.5.1.1.1.13.1 = Temp. 1 of Level 1 EC Box .1.3.6.1.4.1.34550.30.5.1.1.1.13.3 = Humid. 2 .1.3.6.1.4.1.34550.30.5.1.1.1.13.9 = Lamp 1 .1.3.6.1.4.1.34550.30.5.1.1.1.13.13 = Buzzer
.1.3.6.1.4.1.34550.30.5.1.5 | iBoxSensorControl | N/A | N/A
.1.3.6.1.4.1.34550.30.5.1.5.1.0 | SetEnvSensorEnable | Write Only | Activate the sensor of the InfraBox. 1 = Confirm T1 = TH sensor 1 , T2 = TH sensor 2 , W1 = Water 1 , W2 = Water 2 , S1 = Smoke / Shock 1 , S2 = Smoke / Shock 2 , e.g. .T1.1 = Activate the TH sensor 1 S2.1 = Activate Smoke / Shock sensor 2
.1.3.6.1.4.1.34550.30.5.1.5.2.0 | SetEnvSensorDisable | Write Only | Deactivate the sensor of the EC Box. 0 = Confirm T1 = TH sensor 1 , T2 = TH sensor 2 , W1 = Water 1 , W2 = Water 2 , S1 = Smoke / Shock 1 , S2 = Smoke / Shock 2 , e.g. .T1.0 = Deactivate the TH sensor 1 S2.0 = Deactivate Smoke / Shock sensor 2
.1.3.6.1.4.1.34550.30.5.1.5.3.0 | SetEnvSensorTempAlarmThreshold | Write Only | Set the Temp. Alarm Threshold of TH sensor of InfraBox in tenth of degree Celsuis. Range : 0000 to 9999 e.g. L01.T1.0300 = Set Temp. Alarm Threshold of Temp 1 to 30 degree Celsuis L16.T2.0900 = Set Temp. Alarm Threshold of Temp 2 to 90 degree Celsuis
.1.3.6.1.4.1.34550.30.5.1.5.4.0 | SetEnvSensorHumidAlarmThreshold | Write Only | Set the Humid. Alarm Threshold of TH sensor of InfraBox in percent. Range : 001 to 100 e.g. H1.030 = Set Humid. Alarm Threshold of Humid 1 to 30.0% H2.099 = Set Humid. Alarm Threshold of Humid 2 to 99.0%
.1.3.6.1.4.1.34550.30.5.1.5.5.0 | SetLampOperation | Write Only | Set the lamp operation mode of the InfraBox. 0 = disable , 1 = enable ( Always ON ) , 2 = turn on when door is open e.g. L1.1 = enable ( always ON ) the Lamp 1 L1.2 = set the lamp 1 ON / OFF by open / close the front door L2.2 = set the lamp 2 ON / OFF by open / close the door
.1.3.6.1.4.1.34550.30.5.1.5.6.0 | SetEnvSensorEventTrigger | Write Only | Config the output device ( Beacon , alarm-out , buzzer ) when sensor ( TH1 & 2 , Smoke / Shock 1 & 2 , Water 1 & 2 ) alarm is triggered Value syntax : [ Sensor_id ]. [ Beacon_out ] [ Alarm_out ] [Buzzer_out ] Sensor_id : T1 = TH sensor 1 , T2 = TH sensor 2 , S1 = Smoke / Shock sensor 1 , S2 = Smoke / Shock sensor 2 , W1 = Water sensor 1 , W2 = Water sensor 2 Beacon_out : 1 = enable , 0 = disable , Alarm_out : 1 = enable , 0 = disable , Buzzer_out : 1 = enable , 0 = disable e.g. T1.100 = Enable the Beacon out when TH sensor 1 of InfraBox is over the alarm threshold T2.011 = Enable the alarm out & buzzer out when TH sensor 2 of InfraBox is over the alarm threshold W2.100 = Enable the Beacon out when Water sensor 2 of InfraBox is over the alarm threshold ( The alarm threshold of Water sensor is set to 120 as default and cannot be changed )
.1.3.6.1.4.1.34550.30.5.1.5.7.0 | SetPDUDisable | Write Only | Deactivate PDU of InfraBox. 0 = Disable PDU level : 1 ~ 4 Value Syntax : [ PDU_level ] . [ 0 ] e.g. P1.0 = Deactivate PDU level 1 of InfraBox , P4.0 = Deactivate PDU level 4 of InfraBox
.1.3.6.1.4.1.34550.30.5.1.5.8.0 | SetPDUEnable | Write Only | Activate PDU of InfraBox. 1 = Enable PDU level : 1 ~ 4 Value Syntax : [ PDU_level ] . [ 1 ] e.g. P1.1 = Activate PDU level 1 of InfraBox , P4.1 = Activate PDU level 4 of InfraBox