## Sheet1
OID | Name | Access Type | Description
.1.3.6.1.4.1.34550.2 | fanUnit | N/A | N/A
.1.3.6.1.4.1.34550.2.0 | traps | N/A
.1.3.6.1.4.1.34550.2.0.1 | pduTrap | N/A
.1.3.6.1.4.1.34550.2.0.1.1 | fanUnitConnected | N/A | When fan unit is reconnected, this trap will send out once by default
.1.3.6.1.4.1.34550.2.0.1.2 | fanUnitDisconnected | N/A | When fan unit is disconnected, this trap will send out once by default
.1.3.6.1.4.1.34550.2.0.1.3 | fanUnitSpeedNormal | N/A | When CFM setting of fan unit changed to normal, this trap will send out once by default
.1.3.6.1.4.1.34550.2.0.1.4 | fanUnitSpeedHigh | N/A | When CFM setting of fan unit changed to high, this trap will send out once by default
.1.3.6.1.4.1.34550.2.0.1.5 | fanUnitSpeedMax | N/A | When CFM setting of fan unit changed to max, this trap will send out once by default
.1.3.6.1.4.1.34550.2.0.1.6 | fanUnitAutoCfmActivated | N/A | When auto CFM control of fan unit is activated, this trap will send out once by default
.1.3.6.1.4.1.34550.2.0.1.7 | fanUnitAutoCfmDeactivated | N/A | When auto CFM control of fan unit is deactivated, this trap will send out once by default
.1.3.6.1.4.1.34550.2.0.1.8 | fanUnitBuzzerMuted | N/A | When the buzzer of fan unit is muted, this trap will send out once by default
.1.3.6.1.4.1.34550.2.0.1.9 | fanUnitBuzzerUnmuted | N/A | When the buzzer of fan unit is unmuted, this trap will send out once by default
.1.3.6.1.4.1.34550.2.0.2 | fanKitTrap | N/A
.1.3.6.1.4.1.34550.2.0.2.1 | fanKitSwitchOn | N/A | When fan kit is switch on, this trap wil send out once by default.
.1.3.6.1.4.1.34550.2.0.2.2 | fanKitSwitchOnFail | N/A | When fan kit switch on fails, this trap wil send out once by default.
.1.3.6.1.4.1.34550.2.0.2.3 | fanKitSwitchOff | N/A | When fan kit is switch off, this trap wil send out once by default.
.1.3.6.1.4.1.34550.2.0.2.4 | fanKitSwitchOffFail | N/A | When fan kit switch off fails, this trap wil send out once by default.
.1.3.6.1.4.1.34550.2.0.2.5 | fanKitSpeedOff | N/A | When fan kit speed changes to off, this trap wil send out once by default.
.1.3.6.1.4.1.34550.2.0.2.6 | fanKitSpeedNormal | N/A | When fan kit speed changes to normal, this trap wil send out once by default.
.1.3.6.1.4.1.34550.2.0.2.7 | fanKitSpeedHigh | N/A | When fan kit speed changes to high, this trap will send out once by default.
.1.3.6.1.4.1.34550.2.0.2.8 | fanKitSpeedMax | N/A | When fan kit speed changes to max, this trap will send out once by default.
.1.3.6.1.4.1.34550.2.0.2.9 | fanKitSpeedFail | N/A | Whdn fan kit speed change fails, this trap will send out once by default
.1.3.6.1.4.1.34550.2.0.3 | sensorTrap | N/A
.1.3.6.1.4.1.34550.2.0.3.1 | tSensorConnected | N/A | When temperature sensor is reconnected, this trap wil send out once by default.
.1.3.6.1.4.1.34550.2.0.3.2 | tSensorDisconnected | N/A | When temperature sensor is disconnected, this trap wil send out once by default.
.1.3.6.1.4.1.34550.2.0.3.3 | tSensorReadingOverAlarmThreshold | N/A | When temperature reading alarm is triggered, this trap wil send out once by default.
.1.3.6.1.4.1.34550.2.0.3.4 | tSensorReadingResumeNormal | N/A | When temperature reading alarm is cleared, this trap wil send out once by default.
.1.3.6.1.4.1.34550.2.1 | profile | N/A
.1.3.6.1.4.1.34550.2.1.1 | fanUnitProfile Table | N/A | A list of Fan unit Profile entries
.1.3.6.1.4.1.34550.2.1.1.1 | fanUnitProfileEntry | N/A | An entry providing Fan unit profile information
.1.3.6.1.4.1.34550.2.1.1.1.1 | devicePort | not accessible | The device port for fan unit is 1 and cannot be changed.
.1.3.6.1.4.1.34550.2.1.1.1.2 | fanUnitId | not accessible | The cascaded level of the Fan unit
.1.3.6.1.4.1.34550.2.1.1.1.3 | fanUnitModel | Read Only | The model no. of the fan unit
.1.3.6.1.4.1.34550.2.1.1.1.4 | fanUnitFormFactor | Read Only | The form factor of the fan unit. 1=Rackmount, 2=door mount, 3=raised floor mount
.1.3.6.1.4.1.34550.2.1.1.1.5 | fanKitRows | Read Only | The row size of the fan kit
.1.3.6.1.4.1.34550.2.1.1.1.6 | fanKitColumns | Read Only | The column size of the fan kit
.1.3.6.1.4.1.34550.2.1.1.1.7 | fanUnitSerialNumber | Read Only | The serial number of the fan unit
.1.3.6.1.4.1.34550.2.1.1.1.8 | fanKitFirmware | Read Only | The firmware version of the fan unit
.1.3.6.1.4.1.34550.2.1.1.1.9 | alarmKeepUpDuration | Read Only | When the auto CFM control is enabled, the time waiting for the buzzer sounds when the temperature sensor is in alarm state. Value=10 minutes
.1.3.6.1.4.1.34550.2.1.1.1.10 | alarmResumeDropDownDegree | Read Only | When the auto CFM control is enabled and temperature sensor is in alarm state. The temperature drops under the alarm threshold minus the alarmResumeDropDownDegree within the alarmKeepUpDuration, the fan unit returns to normal state.
.1.3.6.1.4.1.34550.2.1.1.1.11 | sensorPortCount | Read Only | The maximum sensor port of the fan unit. It does not reflect how many sensors are actually connected.
.1.3.6.1.4.1.34550.2.1.1.1.12 | maxSensorLevel | Read Only | The maximum level of sensor per sensor port of the fan unit
.1.3.6.1.4.1.34550.2.1.2 | fanKitProfileTable | N/A | A list of Fan kit Profile entries
.1.3.6.1.4.1.34550.2.1.2.1 | fanKitProfileEntry | N/A | An entry providing fan kit profile information
.1.3.6.1.4.1.34550.2.1.2.1.3 | fanKitId | not accessible | The fan kit ID of the fan unit
.1.3.6.1.4.1.34550.2.1.3 | fanSensorProfileTable | N/A | A list of Fan sensor Profile entries
.1.3.6.1.4.1.34550.2.1.3.1 | fanSensorProfileEntry | N/A | An entry providing fan sensor profile information
.1.3.6.1.4.1.34550.2.1.3.1.3 | fanSensorPort | not accessible | The ID of the sensor port
.1.3.6.1.4.1.34550.2.1.3.1.4 | fanSensorLevel | not accessible | The sensor level of the specific sensor port ID
.1.3.6.1.4.1.34550.2.1.3.1.5 | fanSensorDecimalDigits | Read Only | The number of decimal place for sensor
.1.3.6.1.4.1.34550.2.2 | setting | N/A
.1.3.6.1.4.1.34550.2.2.1 | fanUnitSetting Table | N/A | A list of fan unit setting entries
.1.3.6.1.4.1.34550.2.2.1.1 | fanUnitSettingEntry | N/A | An entry providing fan unit setting information
.1.3.6.1.4.1.34550.2.2.1.1.3 | fanUnitRackTag | Read Write | The name of the fan unit. Value : 1 ~ 32 char & special chars.
.1.3.6.1.4.1.34550.2.2.1.1.4 | fanUnitPositionTag | Read Write | The location of the fan unit. Value : 1 ~ 32 char & special chars.
.1.3.6.1.4.1.34550.2.2.1.1.5 | sensorAutoCFMControl | Read Write | The auto CFM control setting of the temperature sensor. 0=disable, 1=enable
.1.3.6.1.4.1.34550.2.2.2 | fanSensorSettingGroup | N/A
.1.3.6.1.4.1.34550.2.2.2.1 | fanSensorSettingTable | N/A | A list of fan sensor setting entries
.1.3.6.1.4.1.34550.2.2.2.1.1 | fanSensorSettingEntry | N/A | An entry providing fan sensor setting information
.1.3.6.1.4.1.34550.2.2.2.1.1.4 | fanSensorActivation | Read Write | Sensor activation state of the fan unit. 0=disable, 1=enable
.1.3.6.1.4.1.34550.2.2.2.1.1.5 | fanSensorType | Read Write | Type of sensor connected to the sensor port of the fan unit. 1=Temperature sensor
.1.3.6.1.4.1.34550.2.2.2.2 | fanTemperatureSensorSettingTable | N/A | A list of fan temperature sensor setting entries
.1.3.6.1.4.1.34550.2.2.2.2.1 | fanTemperatureSensorSettingEntry | N/A | An entry providing fan temperature sensor setting information
.1.3.6.1.4.1.34550.2.2.2.2.1.5 | temperatureSensorLocation | Read Write | The locaton of temperature sensor.
.1.3.6.1.4.1.34550.2.2.2.2.1.6 | temperatureSensorAlarmThreshold | Read Write | The temperature sensor alarm threshold
.1.3.6.1.4.1.34550.2.2.2.2.1.7 | temperautreSensorRisingAlertThreshold | Read Write | The temperature sensor rising alert threshold
.1.3.6.1.4.1.34550.2.2.2.3 | humiditySensorSettingTable | N/A | A list of fan humidity sensor setting entries
.1.3.6.1.4.1.34550.2.2.2.3.1 | humiditySensorSettingEntry | N/A | An entry providing fan humidity sensor setting information
.1.3.6.1.4.1.34550.2.2.2.3.1.5 | humiditySensorAlarmThreshold | Read Write | The humidity sensor alarm threshold
.1.3.6.1.4.1.34550.2.2.2.3.1.6 | humiditySensorRisingAlertThreshold | Read Write | The humidity sensor rising alert threshold
.1.3.6.1.4.1.34550.2.3 | status | N/A
.1.3.6.1.4.1.34550.2.3.1 | fanUnitStatusTable | N/A | A list of fan unit status entries
.1.3.6.1.4.1.34550.2.3.1.1 | fanUnitStatusEntry | N/A | An entry providing fan unit status information
.1.3.6.1.4.1.34550.2.3.1.1.3 | fanUnitConnection | Read Only | The connection status of the fan unit
.1.3.6.1.4.1.34550.2.3.1.1.4 | fanUnitSpeed | Read Only | The speed ( CFM ) of the fan unit. OFF = 0, Normal = 1, High = 2, Max = 3
.1.3.6.1.4.1.34550.2.3.2 | fanKitStatusTable | N/A | A list of fan sensor status entries
.1.3.6.1.4.1.34550.2.3.2.1 | fanKitStatusEntry | N/A | An entry providing fan sensor status information
.1.3.6.1.4.1.34550.2.3.2.1.4 | fanKitConnection | Read Only | The connection status of the fan kit
.1.3.6.1.4.1.34550.2.3.2.1.5 | fanKitStatus | Read Only | The status of the fan kit. Normal = 0, ON Fail = 1, Off Fail = 2, Speed Fail = 3
.1.3.6.1.4.1.34550.2.3.2.1.6 | fanKitSpeed | Read Only | The speed ( CFM ) of the fan kit. OFF = 0, Normal = 1, High = 2, Max = 3
.1.3.6.1.4.1.34550.2.3.3 | sensorStatusGroup | N/A
.1.3.6.1.4.1.34550.2.3.3.1 | temperatureSensorStatusTable | N/A | A list of fan temperature sensor status entries
.1.3.6.1.4.1.34550.2.3.3.1.1 | temperatureSensorStatusEntry | N/A | An entry providing fan temperature sensor status information
.1.3.6.1.4.1.34550.2.3.3.1.1.5 | temperatureSensorConnection | Read Only | The connection state of temperature sensor.
.1.3.6.1.4.1.34550.2.3.3.1.1.6 | temperatureSensorAlarmState | Read Only | The alarm state of temperature sensor. Normal = 0, Alarm = 1, Rising alert = 2
.1.3.6.1.4.1.34550.2.3.3.1.1.7 | temperautreSensorReading | Read Only | The reading of temperature sensor.
.1.3.6.1.4.1.34550.2.3.3.2 | humiditySensorStatusTable | N/A | A list of fan humidity sensor status entries
.1.3.6.1.4.1.34550.2.3.3.2.1 | humiditySensorStatusEntry | N/A | An entry providing fan humidity sensor status information
.1.3.6.1.4.1.34550.2.3.3.2.1.5 | humiditySensorConnection | Read Only | The connection state of humidity sensor.
.1.3.6.1.4.1.34550.2.3.3.2.1.6 | humiditySensorAlarmState | Read Only | The alarm state of humidity sensor. Normal = 0, Alarm = 1, Rising alert = 2
.1.3.6.1.4.1.34550.2.3.3.2.1.7 | humiditySensorReading | Read Only | The reading of humidity sensor.
.1.3.6.1.4.1.34550.2.3.4 | buzzerStatusTable | N/A | A list of fan buzzer status entries
.1.3.6.1.4.1.34550.2.3.4.1 | buzzerStatusEntry | N/A | An entry providing fan buzzer status information
.1.3.6.1.4.1.34550.2.3.4.1.3 | buzzerMuteSound | Read Only | Reserved
.1.3.6.1.4.1.34550.2.4 | control | N/A
.1.3.6.1.4.1.34550.2.4.1 | fanUnitControlTable | N/A | A list of fan unit control entries
.1.3.6.1.4.1.34550.2.4.1.1 | fanUnitControlEntry | N/A | An entry providing fan unit control information
.1.3.6.1.4.1.34550.2.4.1.1.3 | changeFanUnitSpeed | Read Write | Change the speed of fan kits which have been switched on. Normal = 1 , High = 2, Max = 3.
.1.3.6.1.4.1.34550.2.4.1.1.4 | switchFanUnit | Read Write | Switch On / Off fan unit. On = 1 , Off = 0
.1.3.6.1.4.1.34550.2.4.1.1.5 | addFanUnit | Read Write | Add a new fan unit to the InfraBox. Confirm add = 1
.1.3.6.1.4.1.34550.2.4.1.1.6 | deleteFanUnit | Read Write | Delete a fan unit from the InfraBox. Confirm delete = 1
.1.3.6.1.4.1.34550.2.4.2 | fanKitControlTable | N/A | A list of fan kit control entries
.1.3.6.1.4.1.34550.2.4.2.1 | fanKitControlEntry | N/A | An entry providing fan kit control information
.1.3.6.1.4.1.34550.2.4.2.1.4 | switchFanKit | Read Write | Switch On / Off individual fan kit. Off = 0, On = 1
.1.3.6.1.4.1.34550.2.5 | conformance | N/A
.1.3.6.1.4.1.34550.2.5.1 | compliances | N/A
.1.3.6.1.4.1.34550.2.5.1.1 | compliance | N/A
.1.3.6.1.4.1.34550.2.5.2 | groups | N/A
.1.3.6.1.4.1.34550.2.5.2.1 | fanUnitGroup | N/A | A collection of objects providing basic instrumentation and control of the Fan unit
.1.3.6.1.4.1.34550.2.5.2.2 | fanUnitTrapGroup | N/A | A collection of trap
.1.3.6.1.4.1.34550.2.5.2.3 | fanKitGroup | N/A | A collection of objects providing basic instrumentation and control of the fan kit
.1.3.6.1.4.1.34550.2.5.2.4 | fanSensorGroup | N/A | A collection of objects providing basic instrumentation and control of the fan unit sensor